## Instructions
INSTRUCTIONS
Cradle-to-grave electrical design toolkit. Everything the ribbon does, every cell you type in, and every number it calculates — in order. Keep this tab with the project.
Version 2.10 · SÄZÄN PowerCalc add-in · One chapter per ribbon section, in ribbon order. Ribbon ▸ Help ▸ Instructions jumps to any chapter; the CONTENTS links below do the same.
CONTENTS
01 | Getting Started | How the tool is built, installing it, a ten-step quick start and the colour / cell conventions used on every sheet.
02 | Project | Ribbon ▸ Setup ▸ Project. The project shell, the Dashboard and its Design QA panel.
03 | Load Calc | Ribbon ▸ Setup ▸ Load Calc. Building loads, sections, and sending loads to the panel schedules.
04 | Existing Demand | Ribbon ▸ Setup ▸ Existing Demand. NEC 220.87 from utility bills or a 30-day logging study.
05 | Panel Schedules | Ribbon ▸ Distribution ▸ Panel Schedules. Switchboards, MCCs and panelboards; linking is done in the Distribution Map (chapter 14).
06 | Transformers | Ribbon ▸ Distribution ▸ Transformers. Rows derive themselves wherever a feed changes voltage.
07 | Backup Power | Ribbon ▸ Distribution ▸ Backup Power. Generators, transfer switches and UPS systems.
08 | Feeders | Ribbon ▸ Studies ▸ Feeders. One derived row per feeder: conductor, conduit, OCPD and EGC.
09 | Voltage Drop | Ribbon ▸ Studies ▸ Voltage Drop. Run and cumulative %VD per bus.
10 | Short Circuit | Ribbon ▸ Studies ▸ Short Circuit. Available fault current and AIC adequacy at every bus.
11 | Arc Flash | Ribbon ▸ Safety & Review ▸ Arc Flash. IEEE 1584 incident energy and PPE category per bus.
12 | Studies | Ribbon ▸ Safety & Review ▸ Studies. The combined read-only study view and the full refresh.
13 | Reports | Ribbon ▸ Output ▸ Reports.
14 | Distribution Map | Ribbon ▸ Map ▸ Distribution Map (large button). The one-line tree of the whole project in a task pane.
15 | Reference & Troubleshooting | How the engine works, rules, troubleshooting, the code basis and the appendices.
CHAPTER 01 · GETTING STARTED
How the tool is built, installing it, a ten-step quick start and the colour / cell conventions used on every sheet.
What this is, and how it is built
| Purpose | A single tool that carries an electrical design from first load estimate to issued schedules: NEC Article 220 load calc, existing-building demand, panel/switchboard/MCC schedules, transformers, generator and UPS sizing, short circuit, voltage drop, arc flash, feeder sizing, a combined Studies view, and a printable report.
| How it ships | Two parts, and neither one holds your project data. (1) THE ADD-IN — a ribbon tab and a dockable task pane, loaded by Excel from a hosted manifest. It holds the commands. (2) THE PROJECT TEMPLATE — sazan-project-template.xlsx, which holds all 19 calculation sheets with every cross-sheet formula intact and no project data. You start a project from the template; the add-in drives it. There is a third file, SGI_PowerCalc_Master_v1.xlsm, but it is the AUTHORING master that the template is generated from — only the maintainer opens it.
| The add-in | SAZAN Panel Tree, an Office web add-in. Excel loads it from a manifest pointing at static files hosted over HTTPS, so there is nothing to install per machine beyond registering the catalog once. It adds the SÄZÄN POWERCALC ribbon tab and a task pane you can dock, float and resize. It runs on Excel for Windows, Mac and the web, and it contains no VBA — a task pane cannot run macros. See section 2 to install it.
| The project workbook | A copy of sazan-project-template.xlsx saved under your project name. It opens WHOLE — all 19 calculation sheets, every cross-sheet formula and every defined name already in place. Nothing is copied in on demand, because the Dashboard and the modules reference each other in both directions and no single one of them works alone. It stays a plain .xlsx with no macros, so it emails and archives cleanly.
| The code engines | NEC_Data holds the voltage systems, NEC 240.6 OCPD and fuse sizes, the NEMA receptacle library, NEC Chapter 9 Table 8 conductor properties, K and C constants, load classifications and demand factors, and standard transformer kVA. Energy_Code_Data holds lighting power densities and space types. Every dropdown and every calc in the workbook reads from these two sheets — nothing is hardcoded in a formula. Both ship inside the project template, so each project carries its own copy of the code data.
| The device templates | TPL_Switchboard, TPL_Panelboard and TPL_MCC are master layouts, and all three travel inside the project template. When you create a device, the add-in copies the matching template within your own workbook, renames it to your device tag, and registers it on the Dashboard. Editing a template changes every device created afterwards — never devices already created.
| GEO_MAP | Each template carries a small GEO_MAP block (far right of the sheet, grey 8 pt) listing where its name, voltage, AIC, fault, demand and voltage-drop cells live. The commands read addresses from GEO_MAP instead of hardcoding them, so a template can be re-laid-out without breaking the code. See Appendix A.
| The registry is the spine | Every device you create gets one row in the Dashboard EQUIPMENT REGISTRY, keyed by its tag. Studies, links, roll-ups and reconciliation all find equipment by that tag — never by sheet position. If a device is not in the registry, it does not exist to the rest of the tool.
Install and first-time setup
1 | What you need | Excel 365 on Windows, Mac or the web. The add-in's manifest.xml, and one folder your team can reach — a network share works, and a plain local folder is fine for solo testing. You do NOT need admin rights, you do NOT need macros enabled, and there is nothing to unblock.
2 | Register the catalog — once per machine | Put manifest.xml in that folder. Then File ▸ Options ▸ Trust Center ▸ Trust Center Settings ▸ Trusted Add-in Catalogs. Paste the FOLDER path, not the path to the manifest file itself — this is the step people get wrong. Add catalog, tick Show in Menu, OK, then restart Excel. For a team-wide rollout the maintainer can instead upload manifest.xml in the M365 admin center ▸ Settings ▸ Integrated apps, which pushes it to everyone with no per-machine step.
3 | Insert the add-in | Insert ▸ My Add-ins ▸ SHARED FOLDER tab ▸ SAZAN Panel Tree ▸ Add. The task pane opens docked on the right. Drag its inner edge to resize, drag the header out to float, drag it back to redock — Excel manages the dock itself.
4 | Confirm it loaded | You should see a top-level ribbon tab named SÄZÄN POWERCALC, and the task pane should show the black PANEL TREE band. If the tab is missing, the catalog path is wrong or Excel has not been restarted since — see section 13.
5 | Get the project template | Download sazan-project-template.xlsx from the repository and keep one clean copy somewhere the team can reach. Start every project by COPYING that file. Do not work from an email attachment or a Downloads folder.
6 | Keep the template pristine | Never type project data into the clean copy of the template — it is the source every project starts from, and if it gets polluted every future project inherits it. The same rule applies to the authoring master, SGI_PowerCalc_Master_v1.xlsm, which only the maintainer opens.
Quick start — a project in ten steps
1 | Start from the template | Copy sazan-project-template.xlsx and save it under your project name. It already contains all 19 calculation sheets, every formula and every defined name — there is nothing to build and nothing to import.
2 | Fill the project block | Dashboard ▸ PROJECT INFORMATION: project name, number, client, location, engineer / PE of record, date, revision. Blue-on-grey cells only.
3 | Set the system voltage | Dashboard ▸ ELECTRICAL SYSTEM ▸ System Voltage (dropdown). Everything downstream — nominal V, phase, wires, L-N voltage, voltage class — derives from this one selection. Nothing calculates correctly until it is set.
4 | Set design defaults | Dashboard ▸ DESIGN DEFAULTS: branch and feeder conductor material (Cu/Al), termination temperature rating (60/75/90 °C), conduit type. Then UTILITY SOURCES: one column per service transformer (up to four) — tag, provider, kVA, %Z, X/R and the available fault current from each utility letter. Then BUS TIES for split-bus / main-tie-main boards.
5 | Build the load calc | Ribbon ▸ Load Calc. Areas and W/SF allowances first, then itemized equipment across the twelve category tables. This produces the connected load, the NEC 220 demand load, and the suggested service size.
6 | Existing building? Run 220.87 | Ribbon ▸ Existing Demand — 12-month utility bills, or 30-day logging. The 125 % existing demand feeds the Load Calc renovation line and the spare-capacity check.
7 | Create the distribution equipment | Ribbon ▸ Panel Schedules ▸ New Switchboard / Panelboard / MCC. Work top-down: service equipment first, then subpanels. Each device gets its own tab and a registry row.
8 | Link it together | Ribbon ▸ Panel Schedules ▸ Distribution Map. Select a board, set Fed from, Feed type (Sub-Feed / Feed-Through / Tap) and circuit, then Apply to schedules. Child demand rolls up to the parent, and the parent's fault current propagates down. Crossing a voltage boundary automatically adds and sizes a transformer.
9 | Run the studies | Ribbon ▸ Studies ▸ Refresh Studies. One click does both halves now — it rebuilds Arc Flash and then recalculates the Feeder Schedule. Short Circuit and Voltage Drop need no rebuild at all; they derive themselves from the registry the moment a device appears. Enter the per-bus arc-flash inputs, then run it again.
10 | Check QA and issue | Dashboard ▸ DESIGN QA reads 13 checks. Clear every ✘ and review every ⚠. Then Ribbon ▸ Reports ▸ New Report for the printable summary, and save as .xlsx.
Cell conventions — colour, type and layout
| Blue text on grey fill | YOUR INPUT. These are the only cells you should ever type in. Blue #0000FF on grey #D9D9D9.
| Red text | CALCULATED or LINKED. Never type here. This covers both formulas on the same sheet and cross-sheet links. If a red cell is wrong, the error is upstream — find the blue cell feeding it.
| Teal banner #458A96 | Primary section banner, 16 pt, row height 30.
| Dark / mid grey banner | #606262 and #7E868C — secondary headers and sub-labels.
| Gold #F1B92A | Attention. A gold fill or flag means a value needs to be confirmed, or a limit has been approached.
| Green / ochre | #4DAB51 and #CA7F39 — secondary accents and chart series.
| Typography | Segoe UI throughout. Header rows 16 pt at row height 30; data rows 10 pt at row height 15.
| Number formats | Currency and kVA use thousands separators; zeros display as an em-dash rather than 0; percentages one decimal (0.0%); multiples 0.0x; negatives in parentheses. Years are text, never 2,024.
| Do not restyle | The colors carry meaning for reviewers and for the next engineer to open the file. Do not repaint cells to taste.
The ribbon at a glance
| Tab | SÄZÄN PowerCalc. Groups left to right: SETUP (Project, Load Calc, Existing Demand) · DISTRIBUTION (Panel Schedules, Transformers, Backup Power) · STUDIES (Feeders, Voltage Drop, Short Circuit) · SAFETY & REVIEW (Arc Flash, Studies) · OUTPUT (Reports) · MAP (Distribution Map) · HELP (Instructions). Each section is one large button with a dropdown of its commands; this manual has one chapter per section, in the same order.
| New … / Go To … | "New …" creates the module if it is missing and then opens it; "Go To …" only navigates.
CHAPTER 02 · PROJECT
Ribbon ▸ Setup ▸ Project. The project shell, the Dashboard and its Design QA panel.
Ribbon ▸ Project
| New Project | New Project
| Instructions | Instructions
| Dashboard | Dashboard
Module — Project Dashboard
| PROJECT DASHBOARD | Command centre. Project information, the system voltage that drives everything, design defaults, live module status, the 13-point design QA panel, the utility sources and bus ties, the engine constants, the equipment registry, and panel load reconciliation.
| You enter | PROJECT INFORMATION (B7:B13 labels / C-column values); B14 NEC Edition (2020 / 2023 / 2026, default 2023, name Cfg_NEC) - every code citation on the calculation sheets, templates and Report is a formula that reads NEC_Data CX:DB through NECREF("2023 number"), so choosing 2026 turns 220.87 into 120.87, Article 220 into 120, and so on. Choosing 2026 also enables Load Calc C38 (load being removed, subtracted in the 120.87 renovation check). The 2026 column of the map comes from published summaries - check it against NFPA 70-2026 and edit NEC_Data DA directly; this Instructions tab is written to 2023 numbering. ELECTRICAL SYSTEM: System Voltage dropdown at C37 — this is the single most important input in the workbook. DESIGN DEFAULTS C46:C49 — branch conductor material, feeder conductor material, termination temperature rating (60/75/90), conduit type. CALCULATION MODULES C53:C56 — ON/OFF for breaker sizing (always on), wire sizing, voltage drop, short circuit; C57:C58 — Standby Generator / UPS status (Tog_Gen / Tog_UPS), read-only, set by ribbon ▸ New Generator / New UPS. Neither module is in a project by default: until deployed, the Gen / UPS column in every Load Calc section, the connected-loads block at the foot of the Load Calc and the module tab stay hidden. Pressing the button again offers go to / remove / add another copy; removal is refused while any load is still tagged to it. UTILITY SOURCES C63:F77 — one column per service transformer; row 71 is the available symmetrical RMS fault current from the utility letter, row 74 is the fault duty including bus ties that the Short Circuit study starts from. BUS TIES B82:F85 — tie tag, Bus A, Bus B, normal position and transfer type; the sheet traces each bus to its source, checks that either source can carry both buses, and reports the tie fault duty. Main boards are linked by setting their registry Fed From to a source tag.
| It calculates | C38:C42 derive nominal L-L voltage, phase, wires, L-N voltage and voltage class from C37 by lookup into Volt_Table. ENGINE CONSTANTS C65:C70 derive the ampacity table column, the K constant for voltage drop and the C column for short circuit from your conductor material and termination temperature — these are read-only and must not be typed over.
| Feeds | Everything. Every module, every device tab and every study reads these values through defined names (Cfg_Volt, Cfg_BranchMat, Cfg_FeederMat, Cfg_Temp, Cfg_SCA, Tog_VD, Tog_SC, BranchK, FeederK …).
| Equipment registry | Header row 74; data rows 75:324 — capacity 250 devices, set by Cfg_MaxNodes on NEC_Data. Columns: Tag, Type, Voltage, Fed From, Mains, Demand kVA, Sheet Link, Notes, Feed Type, Feeder Ckt / Space. Type straight into the next unshaded row; the table is only ever as long as the project. Rows are also written automatically when a schedule is created from the ribbon. Voltage MUST be picked from the dropdown or the Transformer, Feeder, Short Circuit and Voltage Drop schedules cannot resolve that device and will silently skip it. Fed From must match another Tag exactly, or read Source for the service entrance. Sheet order is irrelevant — everything is matched by Tag.
| Design QA | Rows 21:33, thirteen checks. See section 8.
| Note | Do not insert or delete rows on the Dashboard. Roughly thirty defined names point at fixed addresses on this sheet.
The Design QA panel
Dashboard rows 19:33. The counter at row 19 tallies pass / review / fail / pending. Nothing is issued until every ✘ is cleared and every ⚠ has been reviewed and accepted with a reason.
1 | System voltage configured | Dashboard config. Fails until C37 is set. Nothing downstream is valid before this.
2 | Building area entered | NEC 220. Requires the LC_Areas table to be populated.
3 | New load calculated | NEC 220. Requires demand load > 0 on the Load Calc.
4 | Suggested service size | NEC 240.6. Confirms a standard rating was found for the design load.
5 | Design amps within service | NEC 240.4. Design amps must not exceed the selected service rating.
6 | Existing service spare (renovation) | NEC 220.87. Only applies where an existing-demand module has been run; reports the spare capacity for new load.
7 | Short-circuit AIC margin | NEC 110.9 / 110.10. Reports the MINIMUM margin across every bus in the Short Circuit table. Negative at any bus is a fail.
8 | Voltage drop within limit | NEC 210.19 / 215.2 informational notes. Checks the project maximum %VD against 3 %.
9 | Arc-flash incident energy | IEEE 1584. Reports the worst-case cal/cm² across all buses against a 40 cal/cm² practical limit.
10 | Feeder conductor / OCPD sizing | NEC 310.16 / 240.6. Counts sized feeders on the Feeder Schedule.
11 | Generator sizing | NEC 700 / 701 / 702. Requires standby loads to have been entered or rolled up.
12 | UPS sizing | Critical power. Requires UPS loads to have been entered or rolled up.
13 | Panel load reconciliation | Every Load Calc Panel Tag must reconcile to the kVA entered on that panel's schedule, within the tolerance at Dashboard K362.
CHAPTER 03 · LOAD CALC
Ribbon ▸ Setup ▸ Load Calc. Building loads, sections, and sending loads to the panel schedules.
Ribbon ▸ Load Calc
| New Load Calc | New Load Calc
| Go To Load Calc | Go To Load Calc
| Add Row | Adds one row to the Load Calc section your cursor is in, keeping the section formatting.
| Trim Empty Rows | Removes empty rows from the bottom of the Load Calc section your cursor is in.
| Add / Remove Section | Load Calc: adds or removes an optional section (Refrigeration, Kitchen, Elevators, EV, Fire, Process). Logging Demand: adds or removes the interval-data blocks and load duration curve.
| Send to Panel | Places the selected Load Calc rows on a panel, switchboard or MCC at the circuit you choose, as live links. Ckts / Placed / Status track what has been moved.
| Refresh Placement | Rescans every schedule and updates the Ckts / Placed / Status columns on Load Calc (picks up circuits cleared or moved on a panel).
| Send to Panel — branch length | The Send to Panel dialog has an optional Branch circuit length (ft). It is written to Length Ft on every circuit placed so the schedule's VD % works straight away. Length Ft stays a manual entry on the schedule, even on rows linked from the Load Calc (those are otherwise locked).
Module — Load Calc
| LOAD CALC | NEC Article 220 service load calculation — the backbone of the project. Two layers: an area-based W/SF baseline, then itemized equipment across twelve category tables.
| You enter — areas | LC_Areas (B7:G8): Space Type (from Energy_Code_Data), SF per Floor, Floors. Total SF, LPD in W/ft² and Lighting W calculate. Grow it with Add Area Rows. Row 9 is the TOTAL BUILDING SF line.
| Lighting power density | LIGHTING POWER DENSITY — WSEC C405.4.2 (rows 11:19). You set the Energy Code jurisdiction (C14, default WSEC — WA State) and the Compliance Method (C15, default Building Area Method). Total Lighting Watts (C16) and Total Building SF (C17) link from the area table; C18 returns the GOVERNING BLENDED LPD in W/ft², and C19 flags lighting-type completeness. This block drives the General Lighting row of the W/SF allowances — do not enter a lighting W/SF by hand.
| You enter — W/SF | LC_WSF (B24:G29): the baseline allowances — Category, W/SF, Applies to SF, Demand Factor. Connected kVA and Demand kVA calculate; row 29 is the TOTAL W/SF LOADS line. Default categories are General Power, Computer Power, General Lighting (fed from the WSEC block above) and General Mechanical & Plumbing. Review these on every project — they are firm-standard starting points, not answers.
| You enter — equipment | Twelve tables, each 21 columns, with these header rows: LC_Site (43), LC_House (50), LC_Dept (56), LC_Refrig (63), LC_Mech (70), LC_Plumb (77), LC_Kitchen (84), LC_Elev (91), LC_EV (98), LC_Data (105), LC_Fire (112), LC_Process (119). Section order (also the ribbon picker numbering): 1 Site / Exterior, 2 House / Misc, 3 Department / Owner, 4 Refrigeration, 5 Mechanical, 6 Plumbing, 7 Kitchen / Food Service, 8 Elevators / Conveying, 9 EV Charging, 10 Data / IT, 11 Fire / Life Safety, 12 Process / Industrial. Columns: No. (the equipment tag, e.g. RTU-1), Description, Qty, Connection, Disconnect NEMA / Frame (A) / Fuse (A) / Supplied By, Recept Type, Load Value, Unit, Volts, Ph, PF, kVA Each, Total kVA, Dedicated Ckt, Gen, UPS, Panel Tag, Notes.
| Dropdown behaviour | Connection includes Fused and Non-Fused Disconnect — the Disconnect group only applies to those. Recept Type self-filters to the NEMA receptacles valid for that row's voltage. Load Value + Unit + Volts + Ph + PF drive kVA Each; Qty drives Total kVA. Gen = Y sends the row to the generator roll-up; UPS = Y sends it to the UPS roll-up. Panel Tag drives the reconciliation table on the Dashboard.
| It calculates | PANEL SPACE COUNTER rows 96:111 — poles by section for 480Y/277V, 208Y/120V and 240/120V (120 V loads appear in BOTH the 208Y and 240 columns; read the column matching your system, and note rows marked Ded. Ckt = N are excluded). Row 108 TOTAL SPACES, 109 design spare %, 110 spaces incl. spares, 111 suggested 42-pole panel count. TOTAL SERVICE LOAD SUMMARY rows 114:136 — connected and demand kVA by source, then: row 127 TOTAL NEW LOAD, 128 largest-motor 25 % adder (430.24), 129 continuous-load 25 % adder (210.20 / 215.3), 130 ADJUSTED DESIGN DEMAND, 131 demand amps at service voltage, 132 design spare %, 133 DESIGN LOAD incl. spare, 134 DESIGN AMPS, 135 SUGGESTED SERVICE SIZE (rounded up to a 240.6 rating), 136 RENOVATION CHECK including existing demand.
| Feeds | LC_DemandTotal, LC_AdjustedDemand, LC_DesignAmps, LC_ServiceSize and LC_TotalSF feed the Dashboard status and QA checks. The generator roll-up (rows 138:150) and UPS roll-up (rows 152:165) feed those two modules — each now breaks down per generator/UPS unit, with tags read from that module's UNITS table, and flags any legacy “Y” row not yet assigned to a unit. Panel Tag feeds Dashboard reconciliation.
| Adding rows | Use Add Rows from the ribbon, or press Tab in the last cell of the last row, or right-click ▸ Insert ▸ Table Rows Above. NEVER drag the table's corner handle — it copies formatting without the formulas.
| Sections not on this project | Use Toggle Section from the ribbon, enter the section number, and confirm. The section collapses into an outline group, greys out, drops out of every total, and does not print. Nothing is deleted. You can also flip the Yes/No flag directly in column Y of the SECTION REGISTRY (Load Calc W5:Z19, title at W5, header row 6, sections on rows 7 to 19) — the totals respond immediately, and the next Toggle Section or Refresh Studies brings the collapse back into sync. Row 11 is a deliberate spacer and holds no section, so match on the section number in column W rather than counting rows.
| NEC basis | Article 220 (parts I–IV), 220.12 lighting, 220.14 receptacles, 220.44 / 220.56 demand factors, 430.24 largest motor, 210.20 / 215.3 continuous, 240.6 standard ratings, 625 EV.
Adding and removing rows
| Use the ribbon | Add Rows / Trim Rows — ONE pair of buttons that acts on whichever table your cursor is in: a Load Calc category table, the building-area table, GEN_Loads on the Generator sheet or UPS_Loads on the UPS sheet. Click inside the table first, then click the button. There are no separate Area / Gen / Equip / UPS buttons; that was an earlier design.
| Manual alternatives that are safe | Press Tab in the last cell of the last row. Or right-click a row inside the table ▸ Insert ▸ Table Rows Above. Both extend formulas, dropdowns and the total row correctly.
| Never do this | Do not drag the table's bottom-right corner handle — it extends formatting but not formulas or data validation, and the total row is left behind. Do not insert or delete whole worksheet rows through a table.
| Trim only removes empties | Trim Rows will not delete a row that contains data. If a row will not trim, clear its contents first.
| Registry capacity | The registry holds 250 devices (rows 75:324), governed by Cfg_MaxNodes on NEC_Data. Do not paste rows in below the table — if you genuinely need more than 250 nodes, raise Cfg_MaxNodes deliberately and re-run New Project.
CHAPTER 04 · EXISTING DEMAND
Ribbon ▸ Setup ▸ Existing Demand. NEC 220.87 from utility bills or a 30-day logging study.
Ribbon ▸ Existing Demand
| New Utility Demand (12 mo) | New Utility Demand (12 mo)
| Go To Utility Demand | Go To Utility Demand
| New Logging Demand (30 day) | New Logging Demand (30 day)
| Go To Logging Demand | Go To Logging Demand
| Add Meter | Add Meter
Module — 12-month utility bills
| EXISTING DEMAND — 12-MONTH UTILITY BILLS | NEC 220.87 existing-load determination from twelve months of billed peak demand. The preferred method whenever a full year of bills exists. Sheet: Utility Demand.
| You enter | Per meter block: the peak demand from each of the twelve monthly bills, in kW (or kVA). Service and meter identification at the top. Multi-meter service — click Add Meter for each additional meter; each gets its own twelve-month block.
| It calculates | Per-meter peak demand, then the RESULTS — NEC 220.87 block at rows 32:42: meters included (34), total existing peak demand as the sum of meter peaks (35), the same in kVA (36) and amps (37), the 220.87 existing load at 125 % × peak in kVA (38) and amps (39), existing service capacity (40), SPARE CAPACITY FOR NEW LOAD (41) and service utilisation % (42). Enter the billed PF per bill where you have it rather than accepting the default (note at row 45).
| Feeds | The Load Calc renovation line (row 136) and QA check 6, existing service spare. Dashboard status row 8.
| NEC basis | 220.87 — Determining Existing Loads. Requires 12 months of data and the 125 % multiplier; the demand must be measured, not estimated.
Module — 30-day logging
| EXISTING DEMAND — 30-DAY LOGGING | NEC 220.87 from a 30-day metered logging study, for use when a full year of bills is unavailable or when a specific tenant / feeder load must be measured. Sheet: Logging Demand.
| You enter | Logging study identification, the metering period, the logged peak demand, and the Seasonal / Periodic Load Adjustment Factor at row 38 — a multiplier that accounts for the heating or cooling season peak not captured in a 30-day window. Leave it at 1.0 only if the logging period genuinely covers the seasonal peak.
| It calculates | RESULTS — NEC 220.87 at rows 40:48: governing peak kW (42), governing peak kVA (43), seasonally adjusted peak kVA (44), the 220.87 existing load at 125 % × adjusted peak (45) and in amps (46), existing service capacity (47) and spare capacity for new load (48).
| Feeds | The Load Calc existing-building section and Dashboard status row 9.
| NEC basis | 220.87 exception — a 30-day recording is acceptable where 12 months of data are not available. Note the code requirement to include the peak of the heating or cooling season.
CHAPTER 05 · PANEL SCHEDULES
Ribbon ▸ Distribution ▸ Panel Schedules. Switchboards, MCCs and panelboards; linking is done in the Distribution Map (chapter 14).
Ribbon ▸ Panel Schedules
| New Switchboard | New Switchboard
| New MCC | New MCC
| New Panelboard | New Panelboard
| Move Circuit | Moves the selected circuit (sub-feed, Load Calc load or manual entry) to the circuit number you choose, or swaps two circuits. Linked rows stay locked; registry and Load Calc tracking follow.
| Toggle Sizing Columns | Shows or hides Length / VD % / Wire columns on the active schedule
| Toggle Circuit Entry Dashboard | Shows or hides the Circuit Entry Dashboard (classification columns) on the active schedule
| Repair Schedule | Restore damaged cells and re-derive the grid map on the active schedule
Overrides and manual entries on every schedule
| Main/Bus Rating override (E12) | Blank = calculated: the next standard size at or above the demand amps, 100 A minimum. Pick a larger size (e.g. 1600 A on a board with 100 A connected) to design the board beyond its load. The override carries through to Horiz. Bus, the board's feeder on the Feeder Schedule (Req. Amp, OCPD, conductor, sets) and the kVA of the transformer serving the board, and shows as "ovr" on the Distribution Map. Shown red if below the calculated minimum. Boards made from an older template gain the box on the next refresh.
| Std Device AIC override (E13) | Blank = calculated from the study and the 10 kA (below 380 V) / 14 kA floor. A value here is used by Short Circuit as the device AIC.
| Bus Bracing / Horiz. Bus overrides (E21 / E22) | Blank = calculated (next standard bracing at or above the worst bus fault; next standard bus at or above the Main/Bus rating). Red if below the calculated value.
| Length Ft (circuit rows) | Manual entry on every circuit row, including rows linked from the Load Calc. Drives the branch VD % column. Send to Panel can fill it in.
| Feeder Length (ft) (D20) | The board's own feeder length, used for the board's fault at bus and feeder voltage drop on the schedule. The Feeder Schedule has its own Length column for the feeder study.
Module — Panel schedules
| PANEL SCHEDULES — SWITCHBOARD / PANELBOARD / MCC | One tab per distribution device, created from the ribbon off one of the three templates — TPL_Switchboard, TPL_Panelboard or TPL_MCC. The tab name IS the device tag.
| You enter — at creation | Ribbon prompts: device tag, system voltage (pick from the numbered list), and frame / bus / circuit size.
| You enter — on the tab | Header block: Fed From, Location, Mounting, Enclosure, Manufacturer, Model, Dimensions, Mains Type (MCB/MLO), Main / Bus Rating, Standard Device AIC, Feeder Length. Circuit rows: description, classification, connected kVA (or HP for motors), length, poles. MCC units add starter type, NEMA size, HOA and overload amps.
| It calculates | Per circuit: FLA, design amps, OCPD trip from 240.6, conductor size from 310.16 with your material and termination temperature, and %VD. Per panel: load summary and NEC 220 demand by classification, connected and demand kVA totals, demand FLA, feeder conductor and OCPD, bus fault current, and the AIC check (OK / UNDER-RATED / enter AIC).
| Feeds | Demand kVA to the registry and to the parent device. Bus fault current and device AIC to Short Circuit. Worst-case circuit %VD to Voltage Drop. Connected kVA total to Dashboard reconciliation.
| Cell locations | Vary by template — read them from the GEO_MAP block on each device tab, or from Appendix A.
| NEC basis | 408 panelboards, 240.6 OCPD ratings, 240.4(D) small-conductor rules, 310.16 ampacity, 220 demand factors, 430 motor circuits, 110.9 / 110.10 interrupting rating.
Linking equipment and transformers
| Work top-down | Create the service equipment first, then each downstream device, then link. Linking a parent that does not exist yet is the most common cause of a broken tree.
| Set voltage before linking | Both devices must have their System Voltage set on their own tab before you link them. Linking a device with no voltage selected is refused outright — earlier versions silently produced a bogus 0 V transformer.
| What a link does | Two things at once. Downstream: the child's demand kVA is written into the parent's schedule as a sub-panel load, so it counts in the parent's total. Upstream: the parent's bus fault current is written into the child's source-fault cell, so the child's fault study and AIC check are correct.
| Link / Sub-Feed / Feed-Thru | Link Equipment = fed from a breaker in the parent (consumes poles). Sub-Feed = sub-feed lug tap off the bus (no poles). Feed-Thru = fed through the parent's feed-through lugs at the far end of the bus. Electrically identical roll-up; different pole accounting and different notes on the schedule.
| Crossing a voltage boundary | If parent and child voltages differ, a transformer row is added to the Transformer Schedule and sized from the child's demand, rounded up to the next standard kVA. Go to the Transformers tab and confirm the kVA and impedance.
| After every link | Run Refresh Studies, then Refresh Feeders.
Panel load reconciliation
| PANEL LOAD RECONCILIATION | The audit that catches the most common real error: load assigned to a panel on the Load Calc that was never actually entered on that panel's schedule — and panels carrying load the calc does not know about. Dashboard rows 328 onward; header row 331, data from row 333.
| It calculates | Column A lists every unique Panel Tag used anywhere on the Load Calc automatically. Column C sums the Total kVA assigned to that tag. Column E is the difference against column D, and column F reports OK or CHECK against the match tolerance at K337 (default 0.1 kVA). A CHECK row is highlighted across its full width.
| You enter | Column B — the device Type (Panelboard / MCC / Switchboard). Column D — the connected kVA actually entered on that panel's schedule; a GOLD cell here means the link is not set yet. Column G writes out the exact link formula for you; copy that text and paste it into column D on the same row. The helper block at J332:K335 lists which cell holds the connected total for each device type (Panelboard M69, MCC C47, Switchboard C49).
| Feeds | Dashboard QA check 13.
| Why it matters | A tag typo, or equipment assigned to a panel that was never created, shows up here as a CHECK and nowhere else in the workbook.
CHAPTER 06 · TRANSFORMERS
Ribbon ▸ Distribution ▸ Transformers. Rows derive themselves wherever a feed changes voltage.
Ribbon ▸ Transformers
| New Transformers | New Transformers
| Go To Transformers | Go To Transformers
Module — Transformers
| TRANSFORMERS | Transformer schedule. SELF-DERIVING — rows appear by formula when a link crosses a voltage boundary. No macro writes to this sheet.
| You enter | Very little. Verify the auto-selected standard kVA and the impedance; override if the design or a vendor submittal requires. Add primary and secondary OCPD if not auto-sized.
| It calculates | Required kVA from the child's demand, rounded up to the next standard rating from the Xfmr table in NEC_Data; primary and secondary full-load amps; and the transformer impedance used downstream as a fault-current bottleneck. Each transformer also produces TWO feeder rows on the Feeder Schedule — source to primary, secondary to equipment.
| Feeds | Short Circuit (the transformer is a fault-current bottleneck) and Voltage Drop.
| NEC basis | Article 450 — 450.3 overcurrent protection, 450.11 marking. Standard kVA ratings from the Xfmr table in NEC_Data.
CHAPTER 07 · BACKUP POWER
Ribbon ▸ Distribution ▸ Backup Power. Generators, transfer switches and UPS systems.
Ribbon ▸ Backup Power
| New Generator | New Generator
| Go To Generator | Go To Generator
| New Transfer Switch | Create or remove an ATS / MTS between the normal source and a board, with the generator as its emergency source. Rated and WCR-checked automatically
| New UPS | New UPS
| Go To UPS | Go To UPS
| New UPS System | Place a UPS unit between its input board and the critical board it feeds, or take it out. Rating, input / output OCPD, bypass and SCCR size themselves on the UPS sheet.
How backup equipment sits in the distribution
| Own nodes, never a replacement | A generator, transfer switch or UPS gets its own registry row and its own Distribution Map node. It is inserted between the board that feeds it and the board it serves; no other board is renamed or replaced.
| New UPS System dialog | Output (critical) board · Input from (default: the output board's present breaker; pick another board to feed the UPS from a new breaker there) · UPS input voltage · Internal transformer (Yes = the UPS converts its input voltage to the output board voltage) · If the input board voltage differs: create a transformer ahead of the UPS (T-<UPS>, added to the Transformers schedule and the map) or stop · Bypass.
| UPS rating / SCCR overrides | Set on UPS ▸ UPS SYSTEMS: column K Rating Override (kVA) and column V SCCR Override (A). Blank = calculated.
| Transfer switch overrides | Rating and WCR overrides are in the New Transfer Switch dialog and on Generator ▸ TRANSFER SWITCHES.
Module — Generator
| GENERATOR — BACKUP POWER | Standby / emergency / optional-standby generator sizing from running and starting load. Sheet: Generator.
| You enter | Header: generator type (emergency 700 / legally required 701 / optional 702), fuel, location, ambient and altitude derating. GEN_Loads table (B26:L36): Description, Load Class, Qty, kW each, PF, Start Method, Notes, Unit. The Unit column assigns each load to a generator tag (G-1, G-2 …) from the UNITS table, so one project can size several sets. Or roll loads up automatically from the Load Calc by setting Gen = Y on equipment rows — then assign each to a unit.
| It calculates | kW total and kVA per row; then the SIZING SUMMARY: total running kVA (row 36), total running kW (37), max single-step starting kVA (38), required kW as the sum of per-unit running kW × margin (39), required kVA (40), TOTAL SUGGESTED GENERATOR in kW across all units (41) and total generator kVA at rated PF (42). Start method drives the starting-kVA multiplier — across-the-line is the worst case (×6 typical); soft start / VFD reduce it. Confirm the multipliers at row 44 against real vendor data.
| Feeds | Dashboard status row 10 and QA check 11.
| NEC basis | Articles 700, 701, 702; 445 generator conductors; 220 for the served load. Starting kVA per NEMA MG 1 code letters.
Module — UPS
| UPS — BACKUP POWER | Uninterruptible power supply sizing for critical loads. Sheet: UPS.
| You enter | Header: topology, required runtime, redundancy (N, N+1, 2N), battery type. UPS_Loads table (B26:G34): Description, Qty, kVA each, Notes, Unit. The Unit column assigns each load to a UPS tag (U-1, U-2 …) so several modules can be sized on one project. Or set UPS = Y on Load Calc equipment rows to roll them up, then assign each to a unit.
| It calculates | kVA total per row; then the SIZING SUMMARY: total critical load kVA (row 34), critical load kW at output PF (35), required module kVA as the sum of per-unit load × margin (36), TOTAL SUGGESTED UPS kVA across all units (37) and the resulting module configuration (38). Battery and runtime sizing is NOT calculated here — take it from manufacturer data (note at row 40).
| Feeds | Dashboard status row 11 and QA check 12.
| Basis | Not an NEC sizing article — this is a critical-power design calculation. Verify against the UPS manufacturer's kW/kVA derating and battery runtime curves.
CHAPTER 08 · FEEDERS
Ribbon ▸ Studies ▸ Feeders. One derived row per feeder: conductor, conduit, OCPD and EGC.
Ribbon ▸ Feeders
| New Feeder Schedule | New Feeder Schedule
| Go To Feeder Schedule | Go To Feeder Schedule
| Refresh Feeders | Recalculate and validate the Feeder Schedule — it derives its own rows from the equipment registry.
Module — Feeder Schedule
| FEEDER SCHEDULE | Conductor, conduit, OCPD and equipment grounding conductor for every feeder run. Sheet: Feeder Schedule. SELF-DERIVING: one row per feeder is generated by formula from the equipment registry, including the TWO feeders a voltage change creates — source to transformer primary, then transformer secondary to equipment.
| You enter | Header row 4, data from row 5. MOST COLUMNS ARE DERIVED and must not be typed into. The input columns are H Length (ft), J Cont.?, L Material, M Conduit Type, N EXIST? and W Notes — plus the override columns X Ovr Sets, Y Ovr Conductor, Z Ovr Conduit and AA Ovr Ground, for when a result has to be forced against what the sizing derives.
| It calculates | A Feeder Code and B Feeder Tag, C From and D To, E Load (kVA), F Volts, G Ph and I Design (A) all come from the registry. Then K Req. Amp. from 240.6; O Sets and P Conductor (ea) from 310.16 at your termination temperature; Q Conduit Size by fill; R OCPD; S Ground from 250.122; T %VD @ Std and U %VD Final; and V Status.
| Feeds | Dashboard QA check 10. Refreshed by its OWN button — Refresh Feeders. Refresh Studies does not touch it.
| NEC basis | 215 feeders, 240.6 ratings, 240.4 protection of conductors, 310.16 ampacity, 310.15(C)(1) adjustment, Chapter 9 Tables 1/4/5 conduit fill, 250.122 EGC sizing.
CHAPTER 09 · VOLTAGE DROP
Ribbon ▸ Studies ▸ Voltage Drop. Run and cumulative %VD per bus.
Ribbon ▸ Voltage Drop
| New Voltage Drop | New Voltage Drop
| Go To Voltage Drop | Go To Voltage Drop
| Refresh Voltage Drop | Recalculates Voltage Drop, opens it and lists every bus over the feeder or total limit and every bus still missing feeder data.
Module — Voltage Drop
| VOLTAGE DROP | Feeder voltage drop to every bus, and the cumulative drop back to the source. Sheet: Voltage Drop. SELF-DERIVING from the Short Circuit spill — nothing to rebuild, nothing to type.
| One derived table | Header row 4, data from row 6, one row per bus in tier order. A Node, B Type, C Tier, D Bus Voltage, E Fed From, F Feeder to Bus, G Run %VD, H Cumulative %VD, I Feeder Limit, J Total Limit, K Status, L Notes. The older manual CKT-by-CKT table is gone.
| You enter | Nothing on this sheet. Run %VD is looked up from the Feeder Schedule for that bus's feeder; the cumulative figure walks up the Fed From chain. The two limits come from the named cells Cfg_VDFeeder and Cfg_VDTotal, which default to 3% and 5%.
| It calculates | Cumulative %VD is this run's %VD plus the cumulative %VD of the bus feeding it. Status reads PASS, a warning where a single run or the cumulative total exceeds the feeder recommendation, or FAIL where the cumulative total exceeds the overall limit. Missing feeder data is flagged explicitly rather than being treated as zero — a blank upstream reads as incomplete, not as compliant.
| Feeds | Dashboard QA check 8 against the 3 % branch / 5 % total informational limit.
| NEC basis | 210.19(A) IN 4 and 215.2(A)(2) IN 2 — informational notes, not enforceable requirements, but standard firm practice. Chapter 9 Table 8 for circular mils.
CHAPTER 10 · SHORT CIRCUIT
Ribbon ▸ Studies ▸ Short Circuit. Available fault current and AIC adequacy at every bus.
Ribbon ▸ Short Circuit
| New Short Circuit | New Short Circuit
| Go To Short Circuit | Go To Short Circuit
| Refresh Short Circuit | Re-links each board's Std AIC, rating and demand into the registry, recalculates Short Circuit, opens it and lists every bus that fails or is unresolved. Run Refresh Arc Flash afterwards.
Module — Short Circuit
| SHORT CIRCUIT | Available fault current and interrupting-rating margin at every bus. Sheet: Short Circuit. SELF-DERIVING: the whole table spills from the equipment registry in tier order. There is nothing to rebuild and nothing to type into the table itself.
| You enter | Utility data on the starter row above the device table (blue cells): available fault current, X/R, and the service conductor run. Everything below is generated.
| It derives | Header row 4; device rows begin at row 6, one per registered device, in tier order. Columns: A Node, B Type, C Tier, D Bus Voltage, E Fed From, F Upstream Fault (A), G Feeder to Bus, H f, I M, J Bus Fault Sym (A), K Motor FLA (A), L Motor Contrib (A), M Total Fault (A), N X/R, O Asym Peak (A), P I L-N Sym (A), Q Governing Fault (A), R Device AIC (A), S Margin (A), T Result, U Notes.
| It calculates | Point-to-point fault current using the C values from NEC Chapter 9 Table 8 — the C column follows the conductor material set on the Dashboard — together with the transformer impedances from the Transformer Schedule. Motor contribution is added at L, the asymmetrical peak at O follows from X/R, and single-phase centre-tapped buses also get a line-to-neutral fault at P. Column Q is the GOVERNING fault for that bus; S is the margin against the device AIC at R, and T reports the result.
| Feeds | Arc Flash uses these bolted-fault currents as its input. Dashboard QA check 7 reports the minimum AIC margin across every bus.
| NEC basis | 110.9 interrupting rating, 110.10 circuit impedance and short-circuit current rating, 110.24 available fault current field marking.
CHAPTER 11 · ARC FLASH
Ribbon ▸ Safety & Review ▸ Arc Flash. IEEE 1584 incident energy and PPE category per bus.
Ribbon ▸ Arc Flash
| New Arc Flash | New Arc Flash
| Go To Arc Flash | Go To Arc Flash
| Refresh Arc Flash | Rebuilds the Arc Flash table from the Short Circuit bus list, one row per bus, keeping your per-bus inputs (class, gap, working distance, clearing times). Same rebuild as Refresh Studies.
Module — Arc Flash
| ARC FLASH | Incident energy and PPE category per bus, IEEE 1584. Sheet: Arc Flash.
| You generated | Device rows begin at row 24, written by Refresh Studies from the registry, with the bolted fault current linked from Short Circuit.
| You enter | Per bus, in the blue columns: equipment class (switchgear / MCC / panelboard / cable), electrode gap, grounding configuration, working distance, and the protective-device clearing times t1 and t2. These are keyed to the device tag and are PRESERVED every time you refresh — you do not re-enter them.
| It calculates | Arcing current (column J), incident energy at each clearing time (K and L), governing incident energy in cal/cm² (M), arc-flash boundary (N) and PPE category (O).
| Feeds | Dashboard QA check 9 — worst-case incident energy across all buses, checked against the 40 cal/cm² practical limit.
| Basis | IEEE 1584-2018. Clearing times must come from the actual protective-device time-current curves at the calculated arcing current — an assumed clearing time makes the whole result meaningless. NFPA 70E for label content and PPE selection.
CHAPTER 12 · STUDIES
Ribbon ▸ Safety & Review ▸ Studies. The combined read-only study view and the full refresh.
Ribbon ▸ Studies
| Go To Combined Studies | Go To Combined Studies — the read-only view joining Feeder Schedule, Short Circuit and Voltage Drop by bus.
| Refresh Studies | Rebuild the Arc Flash bus table — Short Circuit and Voltage Drop derive themselves and are not modified.
Refreshing the studies
| When | After creating, resizing, retagging, linking or removing any device. Also after changing the available fault current or the conductor material on the Dashboard.
| What Refresh Studies does | Rebuilds ARC FLASH so it has one row per device in the registry, in registry order, and then recalculates the Feeder Schedule. It does not touch Short Circuit or Voltage Drop — those derive themselves and must not be written to.
| What is preserved | Your Arc Flash per-bus entries — equipment class, gap, grounding, working distance, clearing times — are keyed to the device tag and carried across. Add a device, refresh, and the existing buses keep their inputs.
| Refresh Feeders | Runs the Feeder Schedule recalculation on its own. Refresh Studies already does this, so the separate button is only for when you have changed a feeder input and nothing else. It recalculates and reports; it does not rebuild rows.
| Order of operations for arc flash | Refresh Studies → confirm Short Circuit results → enter clearing times on Arc Flash from the actual device curves → Refresh Studies again → read the QA panel.
| Per-study refresh | Refresh Feeders, Refresh Voltage Drop, Refresh Short Circuit and Refresh Arc Flash each run one study on its own and report its flags. Suggested order after a change: Feeders → Voltage Drop → Short Circuit → Arc Flash.
CHAPTER 13 · REPORTS
Ribbon ▸ Output ▸ Reports.
Ribbon ▸ Reports
| New Report | New Report
| Go To Report | Go To Report
| Reconciliation | Reconciliation
Module — Report
| REPORT | One-page printable project summary — service size, connected and demand load, spare capacity, generator and UPS sizing, and worst-case study results. Sheet: Report.
| You enter | Nothing. Every line is a link. Fill in the project block on the Dashboard and it appears here.
| Use | Ribbon ▸ Reports ▸ New Report, then print or Save as PDF. This is the sheet to attach to a basis-of-design narrative or a utility service application.
CHAPTER 14 · DISTRIBUTION MAP
Ribbon ▸ Map ▸ Distribution Map (large button). The one-line tree of the whole project in a task pane.
Using the map
| Open | Click Distribution Map on the ribbon. The pane docks on the right; drag its edge to resize or drag it out to float.
| What each line shows | Boards: Main/Bus rating and demand amps with % of rating ("ovr" when the rating is overridden). Transformers: standard kVA and load kVA. UPS and transfer switches: their rating. Utility sources: kVA.
| Derived nodes | T-<tag> transformers and ⇄ emergency feeds are drawn from the registry automatically. Edit the board below them, not the derived node.
| Selected equipment | Pick a node to see its type, demand, downstream load and status, and to change Fed from, Feed type (Sub-Feed / Feed-Through / Tap), Fed from ckt #, Mains and Spaces. Apply runs the same link engine as the ribbon commands. Rename and Repair are here too.
| Refresh | Re-reads the registry and refreshes each board's rating / demand links. Use it after editing a schedule outside the map.
| Status flags | ✔ OK · ⚠ Parent not in registry · ⚠ Feed type not set · ⚠ Circular feed. A flag means the registry row needs attention, not the schedule.
CHAPTER 15 · REFERENCE & TROUBLESHOOTING
How the engine works, rules, troubleshooting, the code basis and the appendices.
How the engine works
| Calculation order | (1) Dashboard system voltage and design defaults → (2) engine constants (ampacity column, K, C) → (3) Load Calc areas and equipment → (4) device tabs → (5) links and transformers → (6) studies → (7) QA panel and Report. Errors always propagate downstream, never up. Debug from the top.
| Defined names, not cell refs | Cross-sheet formulas use named ranges (Cfg_*, Tog_*, LC_*, Volt_Table, OCPD_Table, K_Cu, K_Al, Equip_Registry …) so that inserting rows does not break links. New Project creates every name it needs; re-running it repairs any that are missing.
| GEO_MAP | Each device template carries a GEO_MAP key/value block naming its own cell addresses. The macros read that block instead of hardcoding addresses — so the templates can be re-laid-out without touching code. See Appendix A.
| The roll-up chain | Circuit kVA → panel connected total → panel NEC 220 demand → parent device sub-panel load → service demand. Each hop is a live link, so a change at a branch circuit reaches the service size without any refresh.
| What needs a refresh | Only the TABLES that are built by macros: Short Circuit, Voltage Drop, Arc Flash (Refresh Studies) and Feeder Schedule (Refresh Feeders). Everything else is live formulas.
| Tag matching | All cross-references are by device tag, never by sheet position. Reordering tabs is harmless. Renaming a tab breaks everything.
Rules — please read
| ⚠ Do not rename a device tab | The tab name IS the device tag. Studies, links, roll-ups and reconciliation all find equipment by tag. Renaming a tab orphans every reference to it. If a tag is wrong, delete the device properly and recreate it.
| ⚠ Do not delete a device tab by hand | Deleting a panel tab directly leaves dead references and phantom links. Correct order: clear the device's row in the Dashboard registry → delete the tab → Refresh Studies → Refresh Feeders.
| ⚠ Do not type in red cells | Red is calculated or linked. Overwriting a red cell breaks the chain silently and the QA panel will not catch it. Fix the blue input upstream instead.
| ⚠ Do not insert or delete rows on the Dashboard | About thirty defined names point at fixed addresses on that sheet.
| ⚠ Do not edit the back-of-house tabs | NEC_Data, Energy_Code_Data and the TPL_* templates. Changing them changes every calculation and every future device.
| ⚠ Keep the master pristine | No project data in the master or add-in, ever.
| ⚠ Never drag a table's corner handle | Use Add Rows.
| ⚠ This tool does not replace engineering judgement | Every output requires review and stamp by the PE of Record. Arc-flash clearing times, transformer impedances and utility fault currents must come from real device data, not defaults.
Troubleshooting
| The ribbon tab is missing | The add-in is not loaded. Check three things in order: that the Trusted Add-in Catalog points at the FOLDER holding manifest.xml and not at the file itself; that Show in Menu is ticked; and that Excel has been fully restarted since you added the catalog. Then Insert ▸ My Add-ins ▸ SHARED FOLDER and add it again.
| A button does nothing | Two causes. Either it is one of the commands not yet built in this release — those announce themselves when clicked rather than failing silently, and section 5 marks them — or Excel is serving cached add-in files. Excel caches hard: close the task pane, clear the Wef folder under %LOCALAPPDATA%\Microsoft\Office\16.0\Wef, and reopen Excel.
| #NAME? in many cells | The workbook is missing defined names, which means it is not a copy of sazan-project-template.xlsx — a blank workbook will do this. Start again from the template; every name the engine needs ships inside it. Do not try to rebuild them by hand.
| #REF! after deleting a tab | A device tab was deleted by hand. Clear its registry row, then Refresh Studies and Refresh Feeders.
| Everything reads zero | System Voltage at Dashboard C37 has not been selected.
| Short Circuit shows "-" for fault or AIC | Almost always the GEO_MAP block on that device tab. Two known causes. The tab was created from an out-of-date template and has no block at all — the block is marked by a cell containing the text GEO_MAP at the top of its key column. Or the key column is HIDDEN: Excel's Find skips hidden cells, so every lookup returned nothing, silently. The resolver now locates the block through the sheet-scoped GEO_MAP name and no longer depends on that column being visible; on a tab that predates the fix, run Rebuild GEO_MAP. If the block is fine, the AIC simply has not been entered on the device tab.
| Voltage Drop shows an absurd number | A device tab is reading the wrong column — confirm its GEO_MAP VD_RANGE matches the actual VD % column on that tab.
| AIC margin is blank | Enter the Standard Device AIC on the device tab header, then Refresh Studies.
| Reconciliation says "link not set" | Column D on the reconciliation row is empty. Copy the formula that column G generates and paste it into column D.
| Reconciliation says CHECK | The kVA assigned to that Panel Tag on the Load Calc does not match the kVA entered on the panel schedule. Usually a tag typo, or equipment assigned to a panel that was never created.
| Refresh Studies is slow | Expected above about a dozen devices — it writes several hundred formulas. The registry now allows up to 250 nodes, so a large project can take appreciably longer; let it finish rather than interrupting it.
| A section will not drop out of the totals | The totals read the include flag in column Y of the SECTION REGISTRY (Load Calc W5:Z19), not row visibility. Hiding rows by hand does nothing to the totals — use Toggle Section, or set the flag to No.
| A collapsed section still prints | It was hidden by hand instead of toggled, so the include flag still says Yes. Unhide it and use Toggle Section, or set column Y to No.
Back of house — do not edit
| NEC_Data | The lookup engine. Voltage systems (Volt_Table), NEC 240.6 standard OCPD and fuse ratings, the NEMA receptacle library keyed by voltage, NEC Chapter 9 Table 8 conductor properties, K constants for voltage drop, C constants for short circuit, load classifications and demand factors, and standard transformer kVA. Every dropdown and every calculation in the workbook reads from here.
| Energy_Code_Data | Lighting power densities and space types by building type, for the LC_Areas table.
| TPL_Switchboard | Switchboard template. Header block rows 5:15. Circuit rows 28:47. Connected kVA total at K15.
| TPL_Panelboard | Panelboard template — 84 circuits, one circuit per row, laid out in two blocks of 42 (rows 28:69 and 70:111). Header block rows 5:15; feed-through loads rows 20:22. Connected kVA total at K15. This replaced the older 42-circuit two-column layout, which is retired.
| TPL_MCC | Motor control centre template. Header block rows 5:15. Unit rows 28:47, with starter type, NEMA size, HOA, overload amps and FLA per unit. Connected kVA total at K15.
| VBA_Code | A reference copy of the legacy VBA source, for review and version control. Informational only — editing it does nothing. It exists ONLY in the authoring master and is not part of the project template; the live code for the legacy path is in that master's VBA project. See Appendix C.
Code and standards basis
| NEC Article 220 | Branch-circuit, feeder and service load calculations. 220.12 lighting, 220.14 receptacles and equipment, 220.44 / 220.56 demand factors, 220.87 existing loads.
| NEC Article 240 | 240.4 protection of conductors, 240.4(D) small-conductor limits, 240.6 standard ratings.
| NEC Article 250 | 250.122 equipment grounding conductor sizing.
| NEC Article 310 | 310.15 / 310.16 ampacity and adjustment factors.
| NEC Articles 408 / 430 / 445 / 450 | Panelboards; motors and motor circuits (430.24 largest motor); generator conductors; transformers.
| NEC Article 110 | 110.9 interrupting rating, 110.10 SCCR, 110.24 available fault current marking.
| NEC Articles 700 / 701 / 702 | Emergency, legally required standby, and optional standby systems.
| NEC Article 625 | Electric vehicle power transfer systems.
| NEC Chapter 9 | Tables 1, 4 and 5 conduit fill; Table 8 conductor properties.
| IEEE 1584-2018 | Arc-flash incident energy calculation.
| NFPA 70E | Arc-flash labelling and PPE selection.
| Energy code | ASHRAE 90.1 / IECC lighting power densities, via Energy_Code_Data.
| Verify the edition | Confirm the adopted NEC and energy-code edition for the project's jurisdiction. NEC_Data must match it.
Appendix A · DEVICE TEMPLATE CELL MAP (GEO_MAP)
Each device tab carries this block, marked by the literal text GEO_MAP in the top-left cell of the key column and also defined as a sheet-scoped name: Switchboard AS1:AX20 · Panelboard AS1:AX34 · MCC BJ1:BO20. Read left to right: SWBD ¦ PANELBOARD ¦ MCC. The header keys are identical on all three templates. The block has six columns: KEY, VALUE, then ANCHOR_TEXT, ANCHOR_COL, TARGET_COL and ROW_OFFSET — Rebuild GEO_MAP finds each key's anchor label in the sheet and rewrites its VALUE from where that label actually sits, which is how a re-laid-out template repairs itself. THE MARKER CELL IS NOT OPTIONAL: Rebuild GEO_MAP locates the block by searching for the text GEO_MAP, and if it is missing the command warns and does nothing. The panelboard block is longer because it also carries the circuit-grid, feed-through and resize keys — CKT_PER_ROW, CKT_DESC_COL, CKT_KVA_COL, CKT_POLES_COL, CKT_NUM_COL, VD_COL, FEEDTHRU_FIRST / LAST / DESC_COL / KVA_COL, FT_SLOTS, BLOCK_SIZE, CKT_BLOCK1 and CKT_BLOCK2 bounds, and RESIZE_MODE.
| NAME_CELL | D5 ¦ D5 ¦ D5 — the device tag / name.
| VOLT_CELL | D8 ¦ D8 ¦ D8 — system voltage selection.
| AIC_CELL | D13 ¦ D13 ¦ D13 — standard device interrupting rating.
| SRCFAULT_CELL | H5 ¦ H5 ¦ H5 — fault current available AT the device (written by a link).
| BUSFAULT_CELL | H6 ¦ H6 ¦ H6 — fault current at this device's own bus (read by children).
| DEMAND_CELL | H10 ¦ H10 ¦ H10 — NEC 220 demand kVA; rolls up to the parent and the registry.
| CONNECTED_CELL | K15 ¦ K15 ¦ K15 — connected kVA total; used by Dashboard reconciliation.
| ENG_VLL_CELL | AQ26 ¦ AQ26 ¦ BH26 — engine line-to-line voltage (numeric).
| ENG_PH_CELL | AQ28 ¦ AQ28 ¦ BH28 — engine phase count (numeric).
| VD_RANGE | K28:K47 ¦ K28:K111 ¦ K28:K47 — the % voltage drop column.
| CKT_FIRST / CKT_LAST | 28–47 ¦ 28–111 ¦ 28–47 — circuit / unit row span. On the panelboard these are DERIVED, not typed: BLOCK_SIZE = 42 and RESIZE_MODE = TWOBLOCK give blocks 28–69 and 70–111, CKT_LAST = 111, and VD_RANGE = VD_COL & CKT_FIRST : VD_COL & CKT_LAST. Change BLOCK_SIZE and re-run Rebuild GEO_MAP rather than editing the bounds by hand.
| If you re-lay-out a template | Update the anchor labels if you renamed them, then run Rebuild GEO_MAP on that sheet — with that sheet ACTIVE — so every value re-anchors itself. Do not change the code. Two traps: if the GEO_MAP marker cell is missing the command silently does nothing but still reports success, and if the KEY and VALUE columns fall out of step every downstream address is wrong by one row. Check the block before blaming the macros.
Appendix B · DEFINED NAME INDEX
| Cfg_* | Dashboard configuration: Cfg_Volt (nominal L-L), Cfg_Phase, Cfg_Wires, Cfg_VLN, Cfg_Class, Cfg_BranchMat, Cfg_FeederMat, Cfg_Temp, Cfg_Conduit, Cfg_SCA (Source 1 available fault current). Utility sources: Util_Tags, Util_Owner, Util_KVA, Util_PriV, Util_SecV, Util_Z, Util_XR, Util_SCA, Util_SCAEff (incl. ties), Util_TagList. Bus ties: Tie_Tags, Tie_BusA, Tie_BusB, Tie_Normal, Tie_Transfer, Tie_SrcA, Tie_SrcB, Tie_Par.
| Tog_* | Module switches: Tog_Breaker, Tog_Wire, Tog_VD, Tog_SC.
| Engine constants | BranchAmpCol, FeederAmpCol, BranchK, FeederK, BranchCCol, FeederCCol — all derived, all read-only.
| LC_* (tables) | LC_Areas, LC_WSF, LC_House, LC_Dept, LC_Refrig, LC_Mech, LC_Plumb, LC_Kitchen, LC_Elev, LC_EV.
| LC_* (results) | LC_TotalSF, LC_ConnectedTotal, LC_DemandTotal, LC_MotorAdder, LC_Continuous, LC_AdjustedDemand, LC_DemandAmps, LC_DesignSpare, LC_DesignLoad, LC_DesignAmps, LC_ServiceSize, LC_RenovationTotal, LC_GenByCategory, LC_GenTotal, LC_UPSByCategory, LC_UPSTotal, LC_SectionState.
| Equipment | Equip_Registry (Dashboard A100:J349, 250 nodes), Equip_List.
| Lookup tables | Volt_Table, OCPD_Table, Fuse_Table, Recept_Table, Cond_Table, Xfmr_Table, K_Cu, K_Al, LPD_Table.
| GEO_MAP | Sheet-scoped, one per device tab. Never delete it.
| Repairing names | Dashboard ▸ New Project re-adds any missing name without altering existing data.
Appendix C · LEGACY — THE VBA MASTER (.xlsm / .xlam)
| Status | LEGACY FALLBACK, maintainer-supported only. The add-in in section 2 is the product. This appendix documents the older macro-driven path, which still works and is kept for desktop users who cannot load a hosted add-in. Do not hand this appendix to a new user as the way in.
| What it is | SGI_PowerCalc_Master_v1.xlsm — the same workbook, with the ribbon driven by a VBA project instead of hosted JavaScript. It also serves as the AUTHORING master: sazan-project-template.xlsx is generated from it by Save As, so the two paths never diverge in their calculations.
| Run it open | Copy the master to a local or network location, open it, and leave it open. The SÄZÄN POWERCALC ribbon tab appears while it is open. Simplest option; good for occasional use.
| Install as an add-in | Preferred for daily use on this path. File ▸ Save As ▸ Excel Add-in (*.xlam). Then File ▸ Options ▸ Add-ins ▸ Manage: Excel Add-ins ▸ Go ▸ Browse ▸ select the .xlam ▸ OK. The ribbon then loads with Excel every time and no extra window stays open.
| Macro trust | This path is macro-enabled, so it needs trust the add-in path does not. If you see the yellow security bar, click Enable Content. If macros are blocked outright (Mark of the Web), right-click the file ▸ Properties ▸ Unblock, or place the file in a Trust Center trusted location. Windows only — the VBA path does not run on Excel for Mac or Excel for the web.
| Which path am I on? | Check the title bar. A file ending .xlsm or .xlam is the legacy path. A .xlsx with a task pane on the right is the add-in path. The two are not meant to be run at the same time: if both are loaded you will see one ribbon tab holding both sets of controls, and it is not always clear which one you clicked.
CHANGE LOG
| v1 | Device templates now carry a GEO_MAP block and the macros read cell addresses from it instead of hardcoding them — this repaired Short Circuit (bus fault and AIC), Voltage Drop (wrong column), panelboard voltage-on-create, panelboard demand roll-up, and fault-current propagation through links. Dashboard status and QA now evaluate every row of each study table rather than only the first device. Project-maximum %VD repointed to the correct cell. Link Equipment now refuses to link a device with no voltage set. Manual rewritten in full.
| v1 — manual sync | Module reference re-verified against the live workbook and corrected: equipment registry is 250 nodes at A75:J324 (was documented as 16 at 75:90) and gained Feed Type and Feeder Ckt / Space columns; panel load reconciliation moved to rows 328 onward with tolerance at K337 (was 97 / K103); Load Calc section tables re-addressed to rows 43/49/56/63/70/77/84/91, LC_WSF to B24:G29, LC_Areas to B7:G8, panel space counter to 96:111 and service summary to 114:136; section registry is W5:Z15. Newly documented: the WSEC C405.4.2 lighting-power-density block on the Load Calc, the per-unit Generator and UPS UNITS assignment, and the logging seasonal adjustment factor. Generator and UPS sizing-summary rows re-pointed.
| v1 — add-in rewrite | Manual rewritten for the SAZAN Panel Tree add-in, which is now the product; the VBA master survives as Appendix C, marked legacy. Sections 1, 2 and 13 rewritten around a hosted manifest and a project template that opens whole, replacing the old two-file master model where four sheets were copied into a blank workbook. TPL_PB_Stacked removed — three templates, not four — and Appendix A re-derived from the live GEO_MAP blocks, which are now six columns wide, marked by a GEO_MAP cell at the top of the key column, and identical in their header keys across all three templates. Refresh semantics corrected throughout: Refresh Studies rebuilds Arc Flash ONLY and also recalculates the Feeder Schedule, while Short Circuit, Voltage Drop, the Transformer Schedule and the Feeder Schedule are all self-deriving. Short Circuit re-addressed to header row 4 / data row 6 with the Governing Fault and line-to-neutral columns documented; Voltage Drop rewritten as one derived cumulative table; Feeder Schedule input columns identified as H, J, L, M, N, W and the X:AA overrides. Studies documented for the first time. Category tables corrected from eight to twelve. Section registry corrected to W5:Z19 and the equipment registry to A75:J324. Unbuilt add-in commands disclosed in section 5. Protection password removed from the footer.
End of manual. Questions, corrections or feature requests: route to the PowerCalc maintainer. Do not patch the master yourself.

## Dashboard
PROJECT DASHBOARD — CRADLE-TO-GRAVE ELECTRICAL DESIGN
Blue text on grey = your inputs. Red = auto-calculated (do not type).
PROJECT INFORMATION
[5 empty] | Module | Status | Key Result | Sheet
Project Name |  |  |  |  | Load Calculation | ○ Pending | — | Load Calc
Project Number |  |  |  |  | Utility Bills 220.87 (12-Month) | ○ Pending | — | Utility Demand
Client |  |  |  |  | Logging 220.87 (30-Day) | ○ Pending | — | Logging Demand
Location |  |  |  |  | Generator Sizing | — not in project | — not in project | Generator
Engineer / PE of Record |  |  |  |  | UPS Sizing | — not in project | — not in project | UPS
Date |  |  |  |  | Panel Schedules | ○ Pending | 0 equipment in registry | (registry below)
Revision |  |  |  |  | Short Circuit / AIC | ○ Pending | — no equipment yet | Short Circuit
NEC Edition | 2023 |  |  |  | Voltage Drop | ○ Pending | — | Voltage Drop
[5 empty] | Arc Flash (IEEE 1584) | ○ Pending | — no equipment yet | Arc Flash
DESIGN QA — CHECKS & VALIDATION
0 pass · 2 review · 0 fail · 12 pending
# | Check | NEC / Basis |  | Result
1 | System voltage configured | Dashboard config |  | ⚠ Set System Voltage on Dashboard
2 | Building area entered | NEC 220 |  | ⚠ Enter areas on Load Calc
3 | New load calculated | NEC 220 |  | — No load entered yet
4 | Suggested service size | NEC 240.6 |  | — pending load
5 | Design amps within service | NEC 240.4 |  | — n/a
6 | Existing service spare (renovation) | NEC 220.87 |  | — n/a (new building)
7 | Short-circuit AIC margin | NEC 110.9 / 110.10 |  | — no equipment yet
8 | Voltage drop within limit | NEC 210.19 / 215.2 IN |  | — no equipment yet
9 | Arc-flash incident energy | IEEE 1584 |  | — no equipment yet
10 | Feeder conductor / OCPD sizing | NEC 310.16 / 240.6 |  | — add feeders
11 | Generator sizing | NEC 700 / 701 / 702 |  | — not in project
12 | UPS sizing | Critical power |  | — not in project
13 | Panel load reconciliation | Dashboard § Panel Load Reconciliation |  | — no panels yet
14 | Load Calc loads placed on panels | Load Calc ▸ Send to Panel |  | — no loads entered
ELECTRICAL SYSTEM
System Voltage (select)
Nominal Voltage (L-L)
Phase
Wires
Voltage (L-N)
Voltage Class
DESIGN DEFAULTS
| Branch Conductor Material | Cu
| Feeder Conductor Material | Cu
| Termination Temp Rating | 75
| Conduit Type | Steel
CALCULATION MODULES
| Breaker Sizing | ON | (always on – core function)
| Wire Sizing | ON
| Voltage Drop | ON
| Short Circuit / AIC | ON
| Standby Generator | OFF | (status only – set by ribbon ▸ New Generator)
| UPS | OFF | (status only – set by ribbon ▸ New UPS)
UTILITY SOURCES — SHORT-CIRCUIT
| Parameter | Source 1 | Source 2 | Source 3 | Source 4
Source Tag
Utility / Provider
Ownership
Transformer Size (kVA)
Primary Voltage (V)
Secondary Voltage (L-L)
Impedance (%Z)
X/R Ratio
Available Fault Current at Secondary (A)
Secondary FLA (A)
Infinite-Bus Fault at Secondary (A)
Fault Duty incl. Bus Ties (A)
Boards Served
Source Check
| Multiple Services (NEC 230.2) | — no source tagged
BUS TIES — SPLIT-BUS / MAIN-TIE-MAIN
# | Tie Breaker Tag | Bus A | Bus B | Normal | Transfer | Sources | Check | Fault Duty (A) | Combined kVA
1
2
3
4
ENGINE CONSTANTS (auto – do not edit)
| Branch ampacity column (>100 A) | 4
| Feeder ampacity column (>100 A) | 4
| Branch K (VD) | 12.9
| Feeder K (VD) | 12.9
| Branch C column (SC) | 9
| Feeder C column (SC) | 9
| Raceway magnetic? (SC) | 1
EQUIPMENT REGISTRY
Tag | Type | Voltage | Fed From | Mains | Demand kVA | Sheet Link | Notes | Feed Type | Feeder Ckt / Space | Std AIC (A) | Alt Source | Panel Conn. kVA | Out Voltage | Rating Ovr (A) | Rating (A) | Demand (A) | Feeder Length (ft) | Xfmr Pri. Length (ft) | Emerg. Feeder Length (ft) | Feeder Material | Conduit Type | Existing Feeder?
Type equipment straight into the next row — the shaded row is the one waiting for input. Rows appear as you add devices, so the table is only ever as long as the project. Tag, Type, Voltage, Fed From, Mains and Demand kVA are also written here automatically when a schedule is created from the ribbon. Voltage must be picked from the dropdown, or the Transformer, Feeder, Short Circuit and Voltage Drop schedules cannot resolve that device and will skip it. Fed From must match another Tag exactly, or say Source for the service entrance — the Feeder Schedule names any device whose Fed From does not resolve. Capacity is 250 devices (Cfg_MaxNodes on NEC_Data).
PANEL LOAD RECONCILIATION
What this does: every Panel Tag used anywhere on the Load Calc sheet is listed automatically, and the kVA assigned to it there is compared against the Connected kVA total on that panel's own schedule — catching loads assigned to a panel that were never built into it, and panels carrying loads the calc does not know about. HOW TO USE IT: set Type in column B, then copy the formula text that appears in column G and paste it into column D on the same row; that links the panel's own Connected total back here. A gold cell in column D means the link is not set yet. Status reads OK within the tolerance in K362, or CHECK when the two disagree — a CHECK row is highlighted across its full width. Feeds QA check #13 above. | [8 empty] | Connected-total cell by type (helper)
Panel Tag | Type | Assigned kVA (Load Calc) | Entered on Panel kVA | Δ Assigned − Entered | Status | Link to paste into column D | Notes
[9 empty] | Type | Cell
— no panel tags assigned — | [8 empty] | Panelboard | M69
[9 empty] | MCC | C47
[9 empty] | Switchboard | C49
[9 empty] | Match tolerance (kVA) | 0.1
Note on E27: SÄZÄN PowerCalc: v1.1: now evaluates every bus in the Short Circuit table, not just the first row.
Note on E28: SÄZÄN PowerCalc: v1.1: repointed from H5 (blank) to H4, the actual project-maximum %VD cell.
Note on E29: SÄZÄN PowerCalc: v1.1: now evaluates every bus in the Arc Flash table, not just the first row.
Note on E30: SÄZÄN PowerCalc: v1.1: counts all sized feeders (H column) instead of reporting only row 6. A6 blank = no feeders yet.
Note on B64: SÄZÄN PowerCalc: One column per utility service transformer. Set each main board's Fed From in the registry to this tag. Use Sources 2–4 for redundant services (e.g., main-tie-main).
Note on B66: SÄZÄN PowerCalc: Utility = utility-owned (scheduled for reference only; NEC 90.2(B)(5)). Owner = customer-owned service transformer (medium-voltage service) — engineer must specify it.
Note on B69: SÄZÄN PowerCalc: Auto: follows the System Voltage selected above. Blank when no voltage is selected.
Note on B72: SÄZÄN PowerCalc: From the utility letter — symmetrical RMS at the transformer secondary. This value governs the short-circuit study for that source. Used only when the SC module is ON.
Note on B74: SÄZÄN PowerCalc: Theoretical maximum through this transformer with an infinite primary. A check against the utility letter only — it does not drive the study.
Note on B75: SÄZÄN PowerCalc: Value the Short Circuit study starts from at this source. Adds partner sources through any tie that can parallel (N.C., closed transition or continuous parallel) and takes the larger source through open-transition ties. Conservative: ignores impedance between the source and the tie.
Note on B78: SÄZÄN PowerCalc: More than one service needs one of the NEC 230.2(A)–(D) conditions and a permanent plaque/directory at each service disconnect per 230.2(E).
Note on B82: SÄZÄN PowerCalc: List each tie between split buses or separate main boards. Bus A/B come from the registry. Normal N.O. + Open transition = interlocked (only two of three breakers closed). Closed transition or continuous parallel means both sources feed the fault, so gear AIC must cover the sum.

## Load Calc
SERVICE LOAD CALCULATION
| Project: | — |  |  |  |  | Service Voltage: | [5 empty] | Date: | 2026-10-27
BASELINE SQUARE FOOTAGE
SECTION REGISTRY — ribbon-controlled (does not print)
[24 empty] | Section | Table | Include | Connected kVA | Gen tag list | UPS tag list | Not placed (loads) | Not placed (kVA)
| Space Type | SF per Floor | Floors | Total SF | LPD (W/ft²) | Lighting W | [17 empty] | 1 Site / Exterior | LC_Site | Yes | 0 | Y | Y | 0 | 0
[24 empty] | 2 House / Misc | LC_House | Yes | 0 | GEN-1 | UPS-1 | 0 | 0
| TOTAL BUILDING SF |  |  | 0 |  | 0 | [17 empty] | 3 Department / Owner | LC_Dept | Yes | 0 |  |  | 0 | 0
[24 empty] | 4 Refrigeration (optional) | LC_Refrig | No | n/a |  |  | 0 | 0
LIGHTING POWER DENSITY — C405.4.2 | [23 empty] | 5 Mechanical | LC_Mech | Yes | 0 |  |  | 0 | 0
[24 empty] | 6 Plumbing | LC_Plumb | Yes | 0 |  |  | 0 | 0
[24 empty] | 7 Kitchen / Food Service (optional) | LC_Kitchen | No | n/a |  |  | 0 | 0
| Energy Code (Jurisdiction) | [22 empty] | 8 Elevators / Conveying (optional) | LC_Elev | No | n/a |  |  | 0 | 0
| Compliance Method | [22 empty] | 9 EV Charging (optional) | LC_EV | No | n/a |  |  | 0 | 0
| Total Lighting Watts (from SF table) | 0 | [21 empty] | 10 Data / IT | LC_Data | Yes | 0 |  |  | 0 | 0
| Total Building SF | 0 | [21 empty] | 11 Fire / Life Safety (optional) | LC_Fire | No | n/a |  |  | 0 | 0
| GOVERNING BLENDED LPD (W/ft²) | 0 | [21 empty] | 12 Process / Industrial (optional) | LC_Process | No | n/a |  |  | 0 | 0
| Lighting Type Completeness | — no areas entered
GENERAL DEMAND ALLOWANCES (W/SF)
| Category | W/SF | Applies to SF | Connected kVA | Demand Factor | Demand kVA
| General Power | 2 | 0 | 0 |  | 0
| Computer Power | 2 | 0 | 0 | 100% | 0
| General Lighting ( C405.4.2) | 0 | 0 | 0 | 100% | 0
| General Mechanical & Plumbing | 15 | 0 | 0 | 100% | 0
| TOTAL W/SF LOADS |  |  | 0 |  | 0
EXISTING BUILDING DEMAND — NEC 220.87 (12-MONTH BILLS OR 30-DAY LOGGING)
| Peak Existing Demand (kW) | 0 |  |  | Method (NEC 220.87)
| Peak Demand (kVA) | 0 |  |  | Existing Service Size (A)
| NEC 220.87 Existing Load = 125% × Peak (kVA) | 0 |  |  | Existing Service Capacity (kVA)
| Spare Capacity on Existing Service (kVA) |  |  |  | Service Utilization (%)
Load Being Removed (kVA) — used only with NEC 2026
Auto-filled from the NEC 220.87 module chosen at right — 12-Month Utility Bills (Utility Demand tab) or 30-Day Metered Logging (Logging Demand tab). Enter the source data on that tab; only the selected method feeds this total.
SITE / EXTERIOR
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
HOUSE / MISCELLANEOUS EQUIPMENT
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
DEPARTMENT / OWNER EQUIPMENT
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
REFRIGERATION EQUIPMENT
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
MECHANICAL EQUIPMENT
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
PLUMBING EQUIPMENT
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
KITCHEN / FOOD SERVICE EQUIPMENT (NEC 220.56)
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
ELEVATORS / CONVEYING (NEC 620.14)
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
EV CHARGING (NEC 625 — 100% Unless EMS)
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
DATA / IT EQUIPMENT
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
FIRE / LIFE SAFETY
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
PROCESS / INDUSTRIAL
No. | Description | Qty | Connection | Disc NEMA | Disc Frame (A) | Disc Fuse (A) | Disc Supplied By | Recept Type | Load Value | Unit | Volts | Ph | PF | kVA Each | Total kVA | Ded. Ckt | Gen | UPS | Panel Tag | Notes | Ckts | Placed | Status
0
| NEC DEMAND FACTOR × SECTION TOTAL = SECTION DEMAND → |  |  |  |  | 1 | [7 empty] | 0 | 0
PANEL SPACE COUNTER — PRELIMINARY RISER PLANNING
|  | 480Y/277V Spaces | 208Y/120V Spaces | 240/120V Spaces
| Section |  |  |  | Rows marked Ded. Ckt = N are excluded. 120V loads appear in BOTH 208Y and 240 families — read the column matching your system.
| Site / Exterior | 0 | 0 | 0
| House / Misc | 0 | 0 | 0
| Department / Owner | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0
| Mechanical | 0 | 0 | 0
| Plumbing | 0 | 0 | 0
| Kitchen / Food Service | 0 | 0 | 0
| Elevators / Conveying | 0 | 0 | 0
| EV Charging | 0 | 0 | 0
| Data / IT | 0 | 0 | 0
| Fire / Life Safety | 0 | 0 | 0
| Process / Industrial | 0 | 0 | 0
| TOTAL SPACES | 0 | 0 | 0
| Design Spare Spaces (%) | 25%
| Spaces incl. Spares | 0 | 0 | 0
| Suggested 42-Pole Panels | 0 | 0 | 0
TOTAL SERVICE LOAD SUMMARY — NEC 220
|  |  | Source | Connected kVA | Demand kVA
|  |  | W/SF Allowances (Power / Lighting / Mech-Plumb) | 0 | 0
|  |  | Site / Exterior | 0 | 0
|  |  | House / Misc | 0 | 0
|  |  | Department / Owner | 0 | 0
|  |  | Refrigeration | 0 | 0
|  |  | Mechanical | 0 | 0
|  |  | Plumbing | 0 | 0
|  |  | Kitchen / Food Service | 0 | 0
|  |  | Elevators / Conveying | 0 | 0
|  |  | EV Charging | 0 | 0
|  |  | Data / IT | 0 | 0
|  |  | Fire / Life Safety | 0 | 0
|  |  | Process / Industrial | 0 | 0
|  |  | TOTAL NEW LOAD | 0 | 0
|  |  | Largest Motor × 25% (NEC 430.24) |  | 0
|  |  | Continuous Loads × 25% — conductor / OCPD sizing (NEC 215.3 / 230.42) — enter continuous kVA → | 0 | 0
|  |  | ADJUSTED DESIGN DEMAND (kVA) |  | 0
Demand Amps @ Service Voltage
|  |  | Design Spare Capacity (%) | 20%
|  |  | DESIGN LOAD incl. Spare (kVA) |  | 0
DESIGN AMPS incl. Spare
SUGGESTED SERVICE SIZE (A) — next standard OCPD per NEC 240.6
|  |  | RENOVATION CHECK — NEC 220.87 Existing + New Demand (kVA) |  | 0
GENERATOR-CONNECTED LOADS (Gen = Y) → GENERATOR MODULE
[5 empty] | Per-unit breakdown (kVA) — tags come from the Generator UNITS table | [5 empty] | Untagged (legacy Y)
|  |  | Section | Connected kVA | GEN-1
|  |  | Site / Exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | House / Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Department / Owner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Mechanical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plumbing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Kitchen / Food Service | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Elevators / Conveying | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EV Charging | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Data / IT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Fire / Life Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Process / Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | TOTAL GENERATOR-CONNECTED (kVA) | 0
|  |  | Unassigned to a unit (legacy “Y”) | 0 | ✓ all generator loads assigned
UPS-CONNECTED LOADS (UPS = Y) → UPS MODULE
[5 empty] | Per-unit breakdown (kVA) — tags come from the UPS UNITS table | [5 empty] | Untagged (legacy Y)
|  |  | Section | Connected kVA | UPS-1
|  |  | Site / Exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | House / Misc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Department / Owner | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Mechanical | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plumbing | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Kitchen / Food Service | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Elevators / Conveying | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | EV Charging | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Data / IT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Fire / Life Safety | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Process / Industrial | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | TOTAL UPS-CONNECTED (kVA) | 0
|  |  | Unassigned to a unit (legacy “Y”) | 0 | ✓ all UPS loads assigned

## Utility Demand
UTILITY DEMAND ANALYSIS — NEC 220.87(1) — 12-MONTH BILLING DATA
| Project: | — |  |  |  | Service Voltage:
SETTINGS
|  | Default Power Factor | 0.9 | Used only when a bill has neither kVAR nor a stated PF.
|  | Assumed Load Factor (optional) |  | If a bill has no metered peak, Peak kW = Avg kW ÷ Load Factor. Leave blank to use metered peaks only.
System Voltage (L-L)
Phase
|  | Existing Service (A) |  | Main breaker / service rating. Leave blank for a new service; capacity in D11 stays blank.
Existing Service Capacity (kVA)
METER 1 | [10 empty] | SÄZÄN PowerCalc ▸ Existing Demand ▸ Add Meter creates another meter section below.
| Meter # |  |  | Source: |  |  | Rate Schedule: |  |  | Serves:
|  |  |  | Utility: | [5 empty] | Metered Board: |  | Board this meter measures — its 125% load lands on that board and rolls up the tree. Blank = service board.
| Cycle | Start Date | End Date | Days | kWh | Avg kW | Peak kW (Bill) | Peak kVAR (Bill) | PF (Bill) | PF Used | Peak kW Used | Peak kVA | Peak A | Notes
| 1 | [8 empty] | 0.9
| 2 | [8 empty] | 0.9
| 3 | [8 empty] | 0.9
| 4 | [8 empty] | 0.9
| 5 | [8 empty] | 0.9
| 6 | [8 empty] | 0.9
| 7 | [8 empty] | 0.9
| 8 | [8 empty] | 0.9
| 9 | [8 empty] | 0.9
| 10 | [8 empty] | 0.9
| 11 | [8 empty] | 0.9
| 12 | [8 empty] | 0.9
| METER PEAK | (enter meter #) |  | Bill-year kWh → | 0 |  |  |  |  | Peak → | 0 | 0 | 0
RESULTS — NEC 220.87 EXISTING LOAD (ALL METERS)
[5 empty] | Meters Included | 1
[5 empty] | Total Existing Peak Demand — Sum of Meter Peaks (kW) | 0
[5 empty] | Total Existing Peak Demand (kVA) | 0
[5 empty] | Total Existing Peak Demand (A) | 0
[5 empty] | NEC 220.87 Existing Load = 125% × Peak (kVA) | 0
[5 empty] | NEC 220.87 Existing Load (A) | 0
Existing Service Capacity (kVA)
Spare Capacity for New Load (kVA)
Service Utilization (%)
NEC 220.87(1): existing load basis requires demand data for a full year (12 consecutive billing cycles). Multi-meter total is the non-coincident sum of each meter's individual peak (conservative).
PF per bill: enter the billed PF directly, or enter Peak kVAR and PF is derived (kW/√(kW²+kVAR²)). Bills with PF below 0.90 flag gold.
PEAK DEMAND PROFILE — BY BILLING CYCLE (ALL METERS)
| Cycle | Month | Peak kVA | Peak Cycle | 125% Mark (kVA)
| 1 | Cycle 1 | 0 | 0 | 0
| 2 | Cycle 2 | 0 | 0 | 0
| 3 | Cycle 3 | 0 | 0 | 0
| 4 | Cycle 4 | 0 | 0 | 0
| 5 | Cycle 5 | 0 | 0 | 0
| 6 | Cycle 6 | 0 | 0 | 0
| 7 | Cycle 7 | 0 | 0 | 0
| 8 | Cycle 8 | 0 | 0 | 0
| 9 | Cycle 9 | 0 | 0 | 0
| 10 | Cycle 10 | 0 | 0 | 0
| 11 | Cycle 11 | 0 | 0 | 0
| 12 | Cycle 12 | 0 | 0 | 0
Bars = all meters' billed peak kVA summed per cycle (month from Meter 1 end dates); gold = peak cycle; red dash = 125% NEC 220.87 existing load (G38).

## Logging Demand
30-DAY LOGGING DEMAND — NEC 220.87(2) — METERING / LOGGING SESSION
| Project: | — |  |  | Service Voltage:
SETTINGS
| Data Source |  | Choose whether results use the logger-reported peaks (manual block) or the raw interval data pasted below.
| Default Power Factor | 0.9 | Used when the logger provides kW only (no kVAR / PF / kVA).
System Voltage (L-L)
Phase
| Existing Service (A) | 0
Existing Service Capacity (kVA)
| Service Source |  | Dashboard utility source this logging session measured. Blank = Source 1.
| Utility / Provider |  | From Dashboard ▸ Utility Sources — enter the provider there.
| Metered Board |  | Board this session measured — its NEC 220.87 load lands on (no board yet) and rolls up the tree. Blank = service board.
MANUAL PEAK ENTRY — FROM LOGGER REPORT
Recording Start Date
Recording End Date
Recording Duration (days)
Recorded Peak kW
Recorded Peak kVAR (optional)
Recorded PF (optional)
| PF Used | 0.9
Peak kVA (manual entry)
RAW INTERVAL DATA — SUMMARY |  |  |  | Paste the logger export exactly as received into the grey columns G to K starting at row 54 — Date, Time, Avg kW, and kVAR / kVA if the logger supplied them. The Date column only needs a value where the day changes; blanks are carried down automatically. Columns B to E derive the timestamp and are locked. Depth is 10,000 intervals, enough for 30 days at 4-minute resolution.
| Records Found | 0
First Timestamp
Last Timestamp
Recording Span (days)
Interval (most common, min)
Max kW (from data)
kVAR Coincident with Peak kW
Max kVA (from data)
Load Factor (avg ÷ peak)
COMPLIANCE & SEASONAL ADJUSTMENT
| Recording taken during period of maximum loading? |  | ⚠ NEC 220.87(2): data must be taken while the building is at its period of maximum loading
| Seasonal / Periodic Load Adjustment Factor | 1 | Multiplier on peak to account for seasonal/periodic loads not energized during the recording (e.g., heating logged in summer). 1.00 = no adjustment.
RESULTS — NEC 220.87 EXISTING LOAD
| Governing Peak kW | 0
| Governing Peak kVA | 0
| Seasonally Adjusted Peak kVA | 0
| NEC 220.87 Existing Load = 125% × Adjusted Peak (kVA) | 0
NEC 220.87 Existing Load (A)
Existing Service Capacity (kVA)
Spare Capacity for New Load (kVA)
Service Utilization (%)
DEMAND PROFILE — LOAD DURATION CURVE
Every interval sorted from highest to lowest demand. A curve that drops away steeply means the peak is a brief spike and the 125% figure is conservative; a flat curve means the load is sustained and the peak is representative. Populates once the logger export is pasted below.
RAW INTERVAL DATA — PASTE LOGGER EXPORT BELOW (kVAR / kVA COLUMNS OPTIONAL)
[5 empty] | PASTE EXACTLY AS RECEIVED → |  |  |  |  | DURATION CURVE DATA — derived, feeds the chart
| Timestamp | kW | kVAR (optional) | kVA (optional) | Date | Time | Avg kW | kVAR (optional) | kVA (optional) | % of Time | kW (sorted desc)

## Generator (hidden)
GENERATOR SIZING — NEC 700 / 701 / 702
| Project: | — |  |  |  | Service Voltage:
SETTINGS
| Generator Rated PF | 0.8 |  | Design Margin (×) | 1.2 |  | Assumed Load PF (kVA→kW) | 0.9 |  | Sizing Basis (ATS & Gen) | Calculated Demand
LOADS FROM LOAD CALC (Gen = Y)
| Section | Connected kVA | Include?
| Site / Exterior | 0 | Y
| House / Misc | 0 | Y
| Department / Owner | 0 | Y
| Refrigeration | 0 | Y
| Mechanical | 0 | Y
| Plumbing | 0 | Y
| Kitchen / Food Service | 0 | Y
| Elevators / Conveying | 0 | Y
| EV Charging | 0 | Y
| Data / IT | 0 | Y
| Fire / Life Safety | 0 | Y
| Process / Industrial | 0 | Y
| TOTAL INCLUDED (kVA) | 0
ADDITIONAL / MANUAL LOADS
| Description | Load Class | Qty | kW each | PF | kW total | kVA | Start Method | Start kVA | Notes | Unit
SIZING SUMMARY
| Total Running kVA |  | 0
| Total Running kW |  | 0
| Max Single-Step Starting kVA |  | 0
| Required kW = Σ per-unit (Running kW × Margin) |  | 0
| Required kVA = Σ per-unit max(Running kVA × Margin, Start kVA) |  | 0
| TOTAL SUGGESTED GENERATOR (kW) — all units / banks |  | —
| Total Generator kVA @ Rated PF |  | —
Starting-kVA multipliers are typical (ATL×6, Soft×3, VFD×1.5). Verify against equipment data; largest single step drives voltage-dip sizing.
GENERATOR UNITS — multi-unit / paralleling
| Unit Tag | Description | Parallel Group | Rated PF | Margin (×) | Load PF | Section kVA | Manual kVA | Running kVA | Running kW | Max Start kVA | Required kW | Required kVA | Bank Req kW | Bank Req kVA | Bank Primary | SUGGESTED kW | Gen kVA @ PF | Absorb untagged? | X"d (pu) | Bank names (edit this list)
| GEN-1 | Standby Generator |  | 0.8 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Y | — | — | Y | 0.15 | BANK-A
|  |  |  | 0.8 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | — | — |  | 0.15 | BANK-B
|  |  |  | 0.8 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | — | — |  | 0.15 | BANK-C
|  |  |  | 0.8 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | — | — |  | 0.15 | BANK-D
|  |  |  | 0.8 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | — | — |  | 0.15 | BANK-E
|  |  |  | 0.8 | 1.2 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | — | — |  | 0.15 | BANK-F
TRANSFER SWITCHES — ATS / MTS (created by ribbon ▸ New Transfer Switch)
| Tag | Type | Poles | SE Rated | Scope | Normal Source | Emergency Source | Load Side | Voltage | Load kVA (basis) | Gen Running kVA | Design A | Calc Rating (A) | Rating Override | RATING (A) | Typ. WCR (A) | WCR Override | WCR Used (A) | Fault at ATS (A) | WCR Check | Basis Override
Rating basis (L6, per-switch override in V): CALCULATED DEMAND = next UL 1008 frame ≥ 1.25 × the larger of the load-side NEC 220 demand and the generator unit's running kVA; the generator carries that demand × Design Margin (NEC 702.4(B)(2)(a) full load transferred). EQUIPMENT RATING = the switch is rated at least the load-side board's main/bus rating (registry Rating A) and the generator carries the full rated kVA (V × A × √3), no margin. WCR values are typical — confirm with the manufacturer. Fault at ATS = worst of the normal (utility) path and the generator's own contribution (kVA / X"d).
Note on M52: Corey McKinnon: SÄZÄN PowerCalc: Required kW / kVA also cover every AUTOMATIC transfer switch (ATS) on this unit at its full load-side demand (Transfer Switches ▸ Load kVA), per NEC 702.4(B)(2) — an automatic optional-standby transfer must carry the full load unless a load-management system is provided. MTS (manual, 702.4(B)(1)) is not forced: size for the loads the user will select.

## UPS (hidden)
UPS SIZING — CRITICAL / CONTINUOUS LOADS
| Project: | — |  |  |  | Service Voltage:
SETTINGS
| UPS Output PF | 0.9 |  | Design Margin (×) | 1.25 | Redundancy | N |  | Runtime Target (min) | 10 |  | Typ. UPS SCCR (A) | 65000
LOADS FROM LOAD CALC (UPS = Y)
| Section | Connected kVA | Include?
| Site / Exterior | 0 | Y
| House / Misc | 0 | Y
| Department / Owner | 0 | Y
| Refrigeration | 0 | Y
| Mechanical | 0 | Y
| Plumbing | 0 | Y
| Kitchen / Food Service | 0 | Y
| Elevators / Conveying | 0 | Y
| EV Charging | 0 | Y
| Data / IT | 0 | Y
| Fire / Life Safety | 0 | Y
| Process / Industrial | 0 | Y
| TOTAL INCLUDED (kVA) | 0
ADDITIONAL / MANUAL LOADS
| Description | Qty | kVA each | kVA total | Notes | Unit
SIZING SUMMARY
| Total Critical Load (kVA) | 0
| Critical Load kW @ Output PF | 0
| Required Module kVA = Σ per-unit (Load × Margin) | 0
| TOTAL SUGGESTED UPS (kVA) — all units | —
| Module Configuration | 1 module
Battery/runtime sizing per manufacturer data at the runtime target. Verify inrush & bypass ratings for downstream panels.
UPS UNITS — multi-module / multi-system
| Unit Tag | Description | Output PF | Margin (×) | Redundancy | Section kVA | Manual kVA | Critical kVA | Critical kW | Required Module kVA | SUGGESTED kVA | Configuration | Absorb untagged?
| UPS-1 | UPS System | 0.9 | 1.25 | N | 0 | 0 | 0 | 0 | 0 | — | 1 module | Y
|  |  | 0.9 | 1.25 | N | 0 | 0 | 0 | 0 | 0 | —
|  |  | 0.9 | 1.25 | N | 0 | 0 | 0 | 0 | 0 | —
|  |  | 0.9 | 1.25 | N | 0 | 0 | 0 | 0 | 0 | —
|  |  | 0.9 | 1.25 | N | 0 | 0 | 0 | 0 | 0 | —
|  |  | 0.9 | 1.25 | N | 0 | 0 | 0 | 0 | 0 | —
UPS SYSTEMS — DISTRIBUTION (created by ribbon ▸ New UPS System)
| Tag (UPS unit) | Input From | Output Board | Bypass | Volts | Output Load (kVA) | Unit Sized (kVA) | Margin (×) | Calc Rating (kVA) | Rating Override (kVA) | RATING (kVA) | Output FLA (A) | Efficiency | Recharge Allow. | Input kVA | Input A | Input OCPD (A) | Output OCPD (A) | Inverter Fault (× FLA) | Inverter Fault (A) | SCCR Override (A) | SCCR Used (A) | Fault at UPS (A) | SCCR Check
[13 empty] | 95% | 15% |  |  |  |  | 2
[13 empty] | 95% | 15% |  |  |  |  | 2
[13 empty] | 95% | 15% |  |  |  |  | 2
[13 empty] | 95% | 15% |  |  |  |  | 2
[13 empty] | 95% | 15% |  |  |  |  | 2
[13 empty] | 95% | 15% |  |  |  |  | 2
[13 empty] | 95% | 15% |  |  |  |  | 2
[13 empty] | 95% | 15% |  |  |  |  | 2
Bypass: with a static / maintenance bypass the upstream fault passes through to the output; with None the output fault is limited to the inverter (× FLA). Typical SCCR and inverter limits — verify with the UPS manufacturer.

## Transformers
TRANSFORMER SCHEDULE | [31 empty] | BACKGROUND CALCULATIONS — collapsed by default; nothing here is an input | [19 empty] | DETECTION — every registry edge where the voltage changes needs a transformer
Auto-created from the Equipment Registry: every feed where the voltage changes generates a transformer, and its row appears here on its own — one row shows when the project has no transformers, then rows appear and disappear as connections change. Everything from Tag through Bonding Jumper is derived and locked. The only inputs on this sheet are Source X/R (S), %Z (T) and Load Loss (U) per row, plus Notes (R) and the override columns (AM:AS). A gold %Z cell means that transformer is still calculating on the NEC_Data default — enter the submittal value. A gold Pri OCPD cell means estimated inrush exceeds 10x the selected device, so check the trip curve. System voltages, standard defaults and the inrush multiplier all live on NEC_Data. Columns V onward are background calculation — grouped and collapsed; expand only to audit. | [51 empty] | — no voltage changes detected — | [5 empty] | Unrecognised registry voltages (add them to the config list)
Identification |  | Voltage |  |  | Capacity |  | Construction |  |  |  |  | Overcurrent Protection |  | Grounding & Bonding |  | Loading & Notes |  | Fault Duty |  |  |  | Design Inputs |  |  | Overrides (blank = use derived) | [26 empty] | Child (Serves) | Parent (fed from) | Pri V | Sec V | Ph | Load kVA | ✓ all voltages recognised
Tag | Serves | Ph | Pri V | Sec V | Load kVA | Std kVA | Pri Conn | Sec Conn | Type / Rise | Taps | Enclosure | Pri OCPD (A) | Sec OCPD (A) | GEC 250.66 | Bonding Jumper 250.102(C)(1) | % Loaded | Notes | %Z total | Sec Fault Sym (A) | Sec AIC Req (A) | Inrush (A) | Source X/R | %Z | Load Loss (kW) | Pri OCPD Override (A) | Sec OCPD Override (A) | Pri Conn Override | Sec Conn Override | Type/Rise Override | Taps Override | Enclosure Override | %R | X/R | %X | Pri FLA (A) | Sec FLA (A) | Pri Avail (A) | %R total | %X total | %Z total | Sec Fault Sym (A) | Asym Peak (A) | Inrush (A) | Sec AIC Req (A) | Sec Sets | Sec Cond (basis) | GEC 250.66 | SBJ 250.102(C)(1) | %Z eff | Src X/R eff | Inrush check
UTILITY / SERVICE TRANSFORMERS — from Dashboard › Utility Sources
Tag | Serves | Ph | Pri V | Sec V | Load kVA | Std kVA | Pri Conn | Sec Conn | Type / Rise | Taps | Enclosure | Pri OCPD (A) | Sec OCPD (A) | GEC 250.66 | Bonding Jumper 250.102(C)(1) | % Loaded | Notes | %Z total | Sec Fault Sym (A) | Ownership
Note on AH2: SÄZÄN PowerCalc: INRUSH MULTIPLIER (× FLA) — how to populate What it is: magnetizing inrush current as a multiple of primary FLA, used to compute column AE. Inrush is a first-cycle transient that decays in a few cycles; the primary OCPD has to ride through it without nuisance tripping, and a generator has to be able to supply it. Where to get it: the manufacturer's inrush curve or test report is authoritative. Dry-type units are usually 8 to 12 x FLA; the default of 10 is a reasonable design value before submittals. Use it to check: • Primary OCPD (column M) — the instantaneous trip setting must sit above the inrush point, or use a magnetic-only / higher-instantaneous device. • Generator sizing — carry this into the Generator tab when a transformer starts on emergency power. • Very lightly loaded transformers on the primary of a small feeder — inrush can exceed the feeder OCPD. Raise it to 12 for conservatism on cast coil or K-rated units. Lower it only against a manufacturer curve. Applies to every row in the schedule.
Note on M6: SÄZÄN PowerCalc: 450.3(B): 125% of primary FLA, next standard size up. Where secondary protection at 125% is provided (column N), the primary device may go up to 250% — enter that size in the Pri OCPD Override (AK) rather than typing over this cell.
Note on N6: SÄZÄN PowerCalc: 450.3(B) secondary protection at 125% of secondary FLA; also satisfies 240.21(C) for the secondary conductors. To force a different device, enter it in the Sec OCPD Override (AL) — do not type over this cell.
Note on W6: SÄZÄN PowerCalc: SOURCE X/R — how to populate What it is: the X/R ratio of everything upstream of the transformer primary (utility + service conductors + any upstream transformers). Used to split the upstream impedance into R and X so the secondary fault is combined vectorially rather than arithmetically. Where to get it: • Utility short-circuit letter — best source. Ask for available fault current AND X/R at the service point. • The upstream transformer's own X/R if this primary is fed from another transformer in this project (see column U of that row). Typical values if you have nothing: • 15 — utility service, medium voltage (the NEC_Data default, conservative for a stiff source) • 6 to 10 — fed from a large upstream transformer • 3 to 6 — fed from a small LV transformer Sensitivity: only a minor effect on the symmetrical fault current in AC. It matters most for the asymmetrical peak in AD, which is what breaker momentary and close-and-latch ratings are checked against. A higher number is more conservative. Leave blank to use the Xfmr_DefXR default on NEC_Data. This is a per-row input — enter it on each transformer's own row.
Note on X6: SÄZÄN PowerCalc: Manufacturer value from the factory test report. 5.75% is a typical LV dry-type default; ANSI C57.12.00 allows ±7.5% tolerance. Verify against the approved submittal.
Note on Y6: SÄZÄN PowerCalc: Total load (copper) loss in kW at rated load, from the test report or cut sheet. When entered, X/R is calculated from it; when blank, X/R falls back to the typical value for the kVA rating.
Note on Z6: SÄZÄN PowerCalc: Optional. Enter a device size here only to override the calculated primary OCPD — for example taking the 250% allowance in Table 450.3(B) when secondary protection is present, or matching an existing device in a renovation. Leave blank and column M calculates.
Note on AA6: SÄZÄN PowerCalc: Optional. Enter a device size here only to override the calculated secondary OCPD — for example matching an existing panel main or a coordination study result. Leave blank and column N calculates.
Note on AH6: SÄZÄN PowerCalc: Calculated from load losses when entered: %R = kW loss / kVA x 100, then X/R = SQRT(%Z^2 - %R^2) / %R. With no losses entered it falls back to the typical LV dry-type value for the kVA rating (NEC_Data BJ:BK) — verify with the submittal.
Note on AL6: SÄZÄN PowerCalc: Available fault current at the primary, linked from the upstream bus when the transformer is created. Blank = infinite bus (conservative).
Note on AM6: SÄZÄN PowerCalc: Transformer %R plus the source resistance referred to the transformer base. Source impedance = (Pri FLA / Pri Avail) x 100, split into R and X using the source X/R in S2.
Note on AO6: SÄZÄN PowerCalc: Vectorial sum of source and transformer impedance — R and X added separately, not arithmetic ¦Z¦ addition.
Note on AP6: SÄZÄN PowerCalc: Symmetrical rms bolted fault at the secondary terminals. This is the value the Short Circuit and Arc Flash sheets consume.
Note on AQ6: SÄZÄN PowerCalc: First-cycle asymmetrical peak from the total X/R — compare against the device momentary / close-and-latch rating.
Note on AR6: SÄZÄN PowerCalc: Magnetizing inrush estimate at the multiplier in U2. Drives primary device selection against nuisance tripping and generator sizing.
Note on AS6: SÄZÄN PowerCalc: Minimum standard interrupting rating for the secondary device, from the calculated symmetrical fault.
Note on AT6: SÄZÄN PowerCalc: Sets needed at 125% of secondary FLA, using 750 kcmil Cu (475 A) as the largest single conductor. Basis for GEC sizing only — the designed feeder is on the Feeder Schedule.
Note on AU6: SÄZÄN PowerCalc: Grounding electrode conductor for the separately derived system, Cu, per Table 250.66 keyed on the secondary phase conductor area.
Note on AV6: SÄZÄN PowerCalc: GEC for the separately derived system, Cu, per Table 250.66. Parallel sets are combined by total circular-mil area.
Note on AW6: SÄZÄN PowerCalc: System bonding jumper per 250.28(D)(1) / Table 250.102(C)(1). Above 1100 kcmil equivalent area the jumper must be at least 12.5% of the largest ungrounded phase area.
Note on AX6: SÄZÄN PowerCalc: Effective transformer %Z used by the calculation chain. Uses the value typed in column R when present, otherwise the Xfmr_DefZ default on NEC_Data so a newly detected transformer still calculates. A blank column R on an active row is flagged gold — enter the submittal value.
Note on AY6: SÄZÄN PowerCalc: Effective upstream X/R used by the calculation chain. Uses the value typed in column Q when present, otherwise the Xfmr_DefXR default on NEC_Data.
Note on A108: SÄZÄN PowerCalc: Utility / service transformers pulled from Dashboard › Utility Sources. Reference only — utility-owned equipment is sized by the utility. Load kVA = registry demand of the boards it serves. Sec Fault Sym = fault duty including bus ties.

## Feeder Schedule
FEEDER & OCPD SIZING SCHEDULE | [26 empty] | FEED TABLE ENGINE — background
Auto-derived from the Equipment Registry: every device with a Fed From generates one feeder, and any feed where the voltage changes generates TWO — parent to transformer primary, then transformer secondary to the device. Sizing runs load → design amps → ×1.25 where continuous → next standard OCPD. That OCPD is the Feeder Code in column A (an N suffix is added automatically when the system carries a neutral), and the code drives Sets, Conductor, Conduit Size and Ground straight from the office standard schedule. Where a run is too long, conductors are upsized to the next code in the same neutral family until voltage drop is within the limit set on Dashboard — %VD @ Std and %VD Final show the before and after, and Status names the code borrowed from. The OCPD itself never changes. Set EXIST? to Y for an existing feeder to remain: the lookups are bypassed, the code reads EXIST, and you record what is actually installed in the grouped Override columns to the right. Those overrides work on any row, not just EXIST ones, and Status flags whenever one is in use. Length, Material, Conduit Type and EXIST? are set in the Distribution Map and stored by tag on the registry (Dashboard R:W), so they cannot drift onto another feeder; a blank Material or Conduit inherits the project default (Dashboard C48 / C50). Enter only Cont.?, Notes and the overrides here. Everything else is derived and locked. Transformer primary and secondary feeders are sized on the transformer's standard kVA rating, not the downstream load, and always at 125% per 450.3(B) whether or not Cont.? is set — so they match the OCPD selected on the Transformer Schedule. Requires Microsoft 365 or Excel for the web. | [26 empty] | — no feeders derived — |  |  |  |  | Orphan check
Identification |  |  |  | Load & System |  |  | Sizing Basis |  |  |  | Materials & Status |  |  | Conductors & Protection |  |  |  |  | Voltage Drop, Status & Notes |  |  |  | Overrides (optional) |  |  |  | From | To | Load kVA | Volts | Ph | ✓ every Fed From resolves to a registry tag
Feeder Code | Feeder Tag | From | To | Load (kVA) | Volts | Ph | Length (ft) | Design (A) | Cont.? | Req. Amp. (A) | Material | Conduit Type | EXIST? | Sets | Conductor (ea) | Conduit Size | OCPD (A) | Ground | %VD @ Std | %VD Final | Status | Notes | Ovr Sets | Ovr Conductor | Ovr Conduit | Ovr Ground | [6 empty] | Volt string | Neutral? | Std code | Std conduit | Std conductors | Std ground | NEC sanity | Std sets | Eff. material | Std cond. size | Final code (VD) | Final sets | Final conductors | Final conduit | Final ground | Final cond. size | Eff. sets | Eff. conductors | Eff. conduit | Eff. ground | Eff. cond. size | Override note | Reg. key | Feed role
Note on K4: Corey McKinnon: SÄZÄN PowerCalc: Required ampacity (NEC 215.2(A)(1) / 215.3 / 240.4). Design A × 125% for continuous loads: rows marked Cont. = Y and transformer primaries/secondaries. UPS feeders are continuous: the INPUT feeder uses 125% of the larger of the row load and the UPS input current (incl. recharge); the OUTPUT feeder uses 125% of the larger of the row load and the UPS rated output FLA, so the conductor is protected by the UPS output breaker. Matches the input / output OCPD on the UPS sheet.

## Short Circuit
SHORT-CIRCUIT / FAULT CURRENT STUDY | [20 empty] | NODE ENGINE — background
Point-to-point fault study, derived automatically: one row per bus from the Equipment Registry and the Feeder Schedule, including a bus for every transformer secondary. Rows are ordered by tier (depth from the utility) so each bus reads its upstream fault from its parent, already calculated above it — no iteration and no macro. Feeder run: f = m × L × I_SCA ÷ (C × n × V), M = 1 ÷ (1+f), I_bus = I_SCA × M. Transformer: I_sec(∞) = I_sec,FLA × 100 ÷ %Z, corrected for finite primary fault. Three-phase runs use m = 1.732 and single-phase runs m = 2, both against the run's LINE-TO-LINE voltage, so the line-to-line current and the line-to-line voltage always pair — this is Bussmann's line-to-line fault case. The line-to-neutral case on a centre-tapped single-phase secondary is calculated too, in its own column pair: half-winding impedance is taken as 1.5x the full-winding %R and 1.2x the full-winding %X, the terminal current is the full transformer kVA at the line-to-neutral voltage over that impedance, corrected for the finite primary fault with the primary source impedance DOUBLED because a single-phase fault travels the primary path out and back, and the run then propagates with m = 2 against the line-to-neutral voltage. Motor contribution is added to the line-to-neutral fault as well as the line-to-line one. Governing Fault is the worse of the line-to-line and line-to-neutral results, and Margin and Result are both measured against it, so a device is never checked against the smaller of the two faults. Motor contribution is added to the bus fault before the interrupting-rating comparison. Enter Motor FLA, Device AIC and Notes; everything else is derived and locked. Requires Microsoft 365 or Excel for the web. | [20 empty] | 1 bus(es) resolved | [10 empty] | Unresolved check
Node |  |  |  |  | Upstream |  | Feeder Effect |  | Fault at Bus |  |  |  | Asymmetrical |  | Line-to-Neutral (1Ø centre-tap) |  | Adequacy & Notes |  |  |  | Node | Parent | Volts | Ph | Type | L-N V | Tier | Ordered node table (Node, Parent, Volts, Ph, Type, Tier) |  |  |  | ✓ every bus traces back to the utility
Node | Type | Tier | Bus Voltage | Fed From | Upstream Fault (A) | Feeder to Bus | f | M | Bus Fault Sym (A) | Motor FLA (A) | Motor Contrib (A) | Total Fault (A) | X/R | Asym Peak (A) | I L-N Sym (A) | Governing Fault (A) | Device AIC (A) | Margin (A) | Result | Notes | Utility Service | — |  |  | Source |  | 0 | Utility Service | — | Source | 0 | [18 empty] | %Z half-winding | f (L-N)
[33 empty] | Length | Material | Conduit | Sets | Conductor | Feeder V | Feeder Ph | Node L-N | Feeder L-N | V calc | m | C const | C note | I sec inf | I pri referred | f xfmr | Motor mult ovr
Utility Service | Source | 0 |  | — |  | — utility service — |  | 1 |  |  |  |  | 15 | [5 empty] | ⚠ enter available fault current (Dashboard)
METHOD
Feeder run: f = m × L × I_SCA ÷ (C × n × V) M = 1 ÷ (1 + f) I_bus = I_SCA × M (m = 1.732 three-phase, 2 single-phase; C = Bussmann constant by conductor size, material and raceway; n = sets per phase; V = line-to-line three-phase, line-to-neutral single-phase)
Transformer: I_sec(∞) = I_sec,FLA × 100 ÷ %Z , then corrected for a finite primary fault: f = I_sec(∞) ÷ (I_pri × V_pri ÷ V_sec), I_sec = I_sec(∞) ÷ (1 + f). %Z and X/R come from the Transformer Schedule; a blank %Z there uses the NEC_Data default and is flagged gold on that sheet.
Asymmetrical peak: I_peak = √2 × I_sym × (1.02 + 0.98 e^(−3 ÷ (X/R))) , for comparison against breaker momentary and close-and-latch ratings. Motor contribution: added to the bus fault at the NEC_Data multiplier before the interrupting-rating comparison, and carried downstream.
Adequacy: device interrupting rating ≥ total available fault at the bus. Series ratings are not used — every device stands on its own rating, so a substituted or untested pairing cannot invalidate the study. Raceway C-values are currently loaded for steel only; a PVC or aluminium raceway is flagged rather than silently calculated with steel constants.
Note on J4: SÄZÄN PowerCalc: Symmetrical fault at this bus on the LINE-TO-LINE basis. f = m x L x I / (C x n x V) with m = 1.732 for a three-phase run and 2 for a single-phase run, V always the run's line-to-line voltage — matching Bussmann's line-to-line worked example, which divides by C x n x 240 on a 240/120 system. The line-to-neutral case is computed separately in the I L-N column; compare devices against Governing Fault, not this column.
Note on P4: SÄZÄN PowerCalc: Line-to-neutral symmetrical fault, for centre-tapped single-phase transformer secondaries only — blank on three-phase buses and on single-phase runs tapped line-to-line, since no neutral exists there. Half-winding impedance per Bussmann: %Z = SQRT((1.5 x %R)^2 + (1.2 x %X)^2) on the full-winding basis. Terminal current = full transformer kVA at the line-to-neutral voltage over that impedance, then corrected for the finite primary fault with the PRIMARY SOURCE IMPEDANCE DOUBLED — a single-phase fault runs the primary path out and back, so its impedance counts twice. Downstream runs propagate with m = 2 against the line-to-neutral voltage. Motor contribution is added here on the same basis as the line-to-line path, so this column and Total Fault are directly comparable.
Note on Q4: SÄZÄN PowerCalc: The worse of Total Fault (line-to-line, including motor contribution) and I L-N. This is the value a device's interrupting rating must clear, and it is what Margin and Result are measured against — on a 120/240 panel the line-to-neutral fault normally governs, and Result says so when it does.
Note on R4: Corey McKinnon: SÄZÄN PowerCalc: Device AIC comes from each schedule's Std Device AIC (D13) via the equipment registry - no hand entry. To use a different rating (e.g. series rated), set the Override (E13) on that schedule.

## Voltage Drop
VOLTAGE DROP CALCULATIONS
Cumulative feeder voltage drop, derived automatically: one row per bus, ordered by tier so each bus adds its own run to its parent's cumulative total — the drop shown is what a load at that bus actually sees, not just the last conductor. Run %VD is read from the Feeder Schedule (Vd = m × K × I × L ÷ CM, K = 12.9 Cu / 21.2 Al); nothing is recalculated here, so the two sheets can never disagree. Limits come from NEC_Data and follow the informational notes to 210.19(A)(1) and 215.2(A)(1) — 3% on feeders, 5% combined. These are design recommendations, not mandatory limits, so exceeding them is flagged rather than blocked. Enter Notes only; everything else is derived and locked. Requires Microsoft 365 or Excel for the web.
Node |  |  |  |  | Voltage Drop |  |  | Compliance & Notes
Node | Type | Tier | Bus Voltage | Fed From | Feeder to Bus | Run %VD | Cumulative %VD | Feeder Limit | Total Limit | Status | Notes
Utility Service | Source | 0 |  | — | — utility service — | 0% | 0% | 3% | 5% | — utility source —
METHOD
Vd = m × K × I × L ÷ (CM × n) %VD = Vd ÷ V (m = 1.732 three-phase, 2 single-phase; K = 12.9 Cu / 21.2 Al Ω·cmil/ft; L = one-way length; CM = circular mils per conductor; n = sets per phase). Calculated once on the Feeder Schedule and read from there, so this sheet and that one cannot drift apart.
Cumulative %VD at a bus = the parent bus cumulative + this feeder's run. Because rows are ordered by tier, each parent is already resolved above its child. Limits are the informational-note recommendations of NEC 210.19(A)(1) and 215.2(A)(1) — 3% feeder, 5% total — and are design guidance rather than mandatory, so they are flagged rather than enforced. Motor-load and branch-circuit drop beyond the last panel is not included here; add it against the 5% total using the cumulative figure at that panel as the starting point.

## Arc Flash
ARC FLASH STUDY — IEEE 1584 EMPIRICAL METHOD
| Project: | —
METHOD & DISCLAIMER
Engine: IEEE 1584-2002 empirical equations (208 V–15 kV). Arcing current, normalized incident energy, distance exponent by equipment class, 1.5× LV factor.
Dual-pass per 1584: incident energy evaluated at 100% and 85% arcing current (t2 = clearing time at reduced current) — worst case governs.
CLEARING TIMES MUST BE VERIFIED AGAINST THE PROTECTIVE DEVICE TCC. Typical values below are placeholders for early design only.
Upgrade path: paste IEEE 1584-2018 Tables 1–5 & 7 coefficients and this engine will be converted to the 2018 model (electrode configs VCB/VCBB/HCB, enclosure size CF).
Results are an engineering guide only — final arc flash study requires PE review. Not for labeling without verification.
TYPICAL DEVICE CLEARING TIMES — GUIDE ONLY, VERIFY AGAINST TCC
Molded-case breaker, instantaneous |  |  | 0.025
Current-limiting fuse (within CL range) |  |  | 0.008
Class RK/J fuse @ high fault |  |  | 0.025
LV power breaker, instantaneous |  |  | 0.05
LV power breaker, short-time delay |  |  | 0.3
MV breaker (5 cyc) + relay |  |  | 0.1
BUS TABLE — INCIDENT ENERGY & ARC FLASH BOUNDARY
Node | Volts | Ibf (kA) | Equip Class | Gap (mm) | Grounding | Work Dist (in) | t1 (s) | t2 @85% (s) | Ia (kA) | E1 (cal/cm2) | E2 (cal/cm2) | E (cal/cm2) | AFB (in) | PPE Cat | Model Check | Notes
Rows are added automatically by SÄZÄN PowerCalc ▸ Refresh Studies.

## Studies
COMBINED STUDIES VIEW — FEEDER, SHORT CIRCUIT & VOLTAGE DROP
Read-only review and printing view. One row per bus, tier-ordered, joining the feeder installed to that bus with its fault-current and voltage-drop results so a single line can be checked end to end. Nothing is calculated here — every value is read from Feeder Schedule, Short Circuit or Voltage Drop, so this sheet can never disagree with them. Use the three filters below to slice by tier, by equipment type, or to show only rows needing attention; the count to the right reports how many buses are showing. Change nothing on this sheet: edit the source schedules and this view follows. Requires Microsoft 365 or Excel for the web.
Tier: | All | Type: | All | Show: | All |  |  | Showing 1 of 1 buses
Bus Identification |  |  |  |  | Feeder Installed | [6 empty] | Short Circuit |  |  |  |  | Voltage Drop |  |  | Overall | BACKGROUND — joined source data, do not edit
Node | Type | Tier | Bus Voltage | Fed From | Feeder Tag | Feeder Code | Sets | Conductor | Conduit Size | Ground | Length (ft) | Bus Fault Sym (A) | Governing Fault (A) | Device AIC (A) | Margin (A) | SC Result | Run %VD | Cum %VD | VD Status | Overall | Node | Type | Tier | Bus Voltage | Fed From | Feeder Tag | Feeder Code | Sets | Conductor | Conduit Size | Ground | Length | Bus Fault | Governing Fault | Device AIC | Margin | SC Result | Run %VD | Cum %VD | VD Status | Overall | Show? | Type filter list | Tier filter list
Utility Service | Source | 0 |  | — | [11 empty] | ⚠ enter available fault current (Dashboard) | 0% | 0% | — utility source — | — utility source — | Utility Service | Source | 0 |  | — | [11 empty] | ⚠ enter available fault current (Dashboard) | 0% | 0% | — utility source — | — utility source — | TRUE | All | All
[42 empty] | FALSE | Source | 0
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE
FALSE

## Report
ELECTRICAL LOAD CALCULATION — SUMMARY (AHJ)
NEC Article 220 service load summary — auto-linked from the workbook. Do not edit; update the source tabs.
PROJECT INFORMATION
Project Name | —
Project No. | —
Client | —
Location | —
Engineer / PE | —
Date | —
Revision | —
System Voltage
SERVICE LOAD SUMMARY — NEC ARTICLE 220
Item | Value | Units | Basis / Reference
Total New Connected Load | 0 | kVA | NEC 220.12 – 220.14
Total New Demand Load | 0 | kVA | NEC 220 Part III
Largest Motor + 25% | 0 | kVA | NEC 430.24
Continuous Loads + 25% | 0 | kVA | NEC 210.20(A) / 215.3
Adjusted Design Demand | 0 | kVA | Demand + motor + continuous adders
Design Spare | 20% | % | Design allowance (Load Calc input)
Design Load incl. Spare | 0 | kVA | Adjusted demand × (1 + spare)
Design Amps @ Service Voltage |  | A | kVA × 1000 ÷ (V × √3)
SUGGESTED SERVICE SIZE |  | A | NEC 240.6(A) standard rating
Existing + New (Renovation) | 0 | kVA | NEC 220.87
EQUIPMENT RECAP
Item | Value | Units | Basis / Reference
Suggested Generator | — | kW | NEC 700 / 701 / 702
Suggested UPS Module | — | kVA | Critical power
Transformers Scheduled | 0 | ea | Transformer Schedule
Total Transformer Capacity | 0 | kVA | Std kVA ratings (NEC 450)
Utility Fault Current Available | — | A | NEC 110.24
AIC Margin at First Bus | — | A | NEC 110.9 / 110.10
Worst-Case Voltage Drop | — | % | NEC 210.19 / 215.2 IN
Max Incident Energy | — | cal/cm² | IEEE 1584
CERTIFICATION
Prepared by |  |  | Professional Engineer Seal
Checked by
Date
Revision

## TPL_Switchboard
[40 empty] | GEO_MAP |  | ANCHOR_TEXT | ANCHOR_COL | TARGET_COL | ROW_OFFSET
SWITCHBOARD SCHEDULE | [39 empty] | NAME_CELL | D5 | Switchboard Name | C | D | 0
Enter loads directly in the CIRCUIT ENTRY DASHBOARD columns (O:W). Classification, breaker, wire size and VD% calculate automatically — no panel link required. | [39 empty] | NAME_OVR_CELL | -
| SWITCHBOARD INFORMATION |  |  |  | FAULT SUMMARY |  |  | LOAD SUMMARY & NEC 220 DEMAND | [31 empty] | VOLT_CELL | D8 | System Voltage | C | D | 0
| Switchboard Name |  |  |  | Source Fault Avail. (A) |  |  | Category | Connected | Demand | [29 empty] | AIC_CELL | D13 | Std Device AIC (A) | C | D | 0
| Fed From | Utility Service |  |  | Fault at Bus (A) |  |  | Lighting | 0 | 0 | [29 empty] | SRCFAULT_CELL | H5 | Source Fault Avail. (A) | G | H | 0
| Location |  |  |  | AIC Check | — |  | Receptacle | 0 | 0 | [29 empty] | BUSFAULT_CELL | H6 | Fault at Bus (A) | G | H | 0
| System Voltage | [6 empty] | Motor | 0 | 0 | [29 empty] | DEMAND_CELL | H10 | Demand Total (kVA) | G | H | 0
| V (L-L / L-N) |  |  |  | FEEDER SUMMARY |  |  | HVAC | 0 | 0 | [29 empty] | CONNECTED_CELL | K16 | TOTALS (kVA) | J | K | 0
| Phase / Wires |  |  |  | Demand Total (kVA) | 0 |  | Electric Heat | 0 | 0 | [29 empty] | ENG_VLL_CELL | AQ27 | engine (do not delete) | AP | AQ | 1
| Mains Type | MCB | Override |  | Demand FLA (A) |  |  | Kitchen Equip | 0 | 0 | [29 empty] | ENG_PH_CELL | AQ29 | engine (do not delete) | AP | AQ | 3
| Main/Bus Rating (A) |  |  |  | Feed |  |  | Continuous | 0 | 0 | [29 empty] | VD_RANGE | K29:K48
| Std Device AIC (A) | 10000 |  |  | Feeder Length (ft) |  |  | General | 0 | 0 | [29 empty] | CKT_FIRST | 29 | CKT | B |  | 1
| Mounting |  |  |  | Feeder Sets |  |  | Sub-Panels / Feed-Thru | 0 | 0 | [29 empty] | CKT_LAST | 48
| Enclosure |  |  |  | Feeder Conductor |  |  | Existing Load (NEC 220.87) | 0 | 0 | [29 empty] | CKT_PER_ROW | 1
| Manufacturer |  |  |  | Feeder OCPD (A) |  |  | TOTALS (kVA) | 0 | 0 | [29 empty] | CKT_DESC_COL | C
| Model / Series | [6 empty] | TOTALS (Amps) | [31 empty] | CKT_CLASS_COL | -
| Dims HxWxD (in) |  | Override |  | PHASE BALANCE | [34 empty] | CKT_QTY_COL | -
| Bus Bracing (kA) | — |  |  | Phase A (kVA) | 0 |  | FEED-THROUGH LOADS | [31 empty] | CKT_KVA_COL | W |  |  |  |  | FEED-THRU DETAIL (managed by Feed-Through — do not edit)
| Horiz. Bus Rating (A) | — |  |  | Phase B (kVA) | 0 |  | Description | Conn. kVA | Demand kVA | [29 empty] | CKT_POLES_COL | E |  |  |  |  | Ph A kVA | Ph B kVA | Ph C kVA | Rcpt conn. kVA | Rcpt dem. kVA
| Wiring Class / Type |  |  |  | Phase C (kVA) | 0 | [31 empty] | VD — upstream cumulative %VD (from study) | 0% | FEEDTHRU_FIRST | 21 | Description | J |  | 1
[5 empty] | Imbalance % | 0% | [31 empty] | VD — branch %VD budget (5% less upstream) | 3% | FEEDTHRU_LAST | 23
[38 empty] | VD — combined worst-case %VD | 0% | FEEDTHRU_DESC_COL | J
[38 empty] | VD — combined status |  | PHASE_A_CELL | H19 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[8 empty] | Subtotal (kVA): | 0 | 0 | [10 empty] | cls factor → | 1.25 | 1 | 1.25 | 1.25 | 1.25 | 1 | 1.25 | 1 | 1 | [7 empty] | engine (do not delete) | engine | PHASE_B_CELL | H20 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[40 empty] | PHASE_C_CELL | H21
CIRCUIT SCHEDULE | [11 empty] | CIRCUIT ENTRY DASHBOARD | [27 empty] | REC_TOT_CELL | AQ38
CKT | Load Description |  | P | Bkr A | Classification | Conn. kVA | HP | Length Ft | VD % | Wire / Gnd | Notes | LTG | REC | MTR | HVC | HEAT | KIT | CONT | GEN | PNL | IsM | CtF | DmT | CktV | FLC | FLA | DesI | OCPDt | Pos | VA# | PhI | vaA | vaB | vaC | OVR | Cons | Sets |  |  | REC_DEM_CELL | AQ39
1 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | FT_CONN_COL | K
2 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 |  |  | FT_DETAIL_COL | AY
3 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 |  |  | BLOCK_SIZE | 20
4 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | FT_SLOTS | 3
5 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | VD_COL | K
6 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | CKT_NUM_COL | B
7 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | FEEDTHRU_KVA_COL | L
8 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Bus bracing — calc. min (kA) |  | CKT_BLOCK1_FIRST | 29
9 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | Horiz. bus — calc. min (A) |  | CKT_BLOCK1_LAST | 48
10 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Receptacle — total conn. incl. feed-thru (kVA) | 0 | CKT_BLOCK2_FIRST | -
11 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Receptacle — combined demand (kVA) | 0 | CKT_BLOCK2_LAST | -
12 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | Feeder — parallel sets (750 kcmil max per set) | 0 | RESIZE_MODE | SINGLE
13 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Std device AIC — calc. min (A) | 10000
14 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Main/Bus — calc. min (A)
15 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
16 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
17 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
18 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
19 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
20 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
NOTES
1 | X
2 | X
3 | X
4 | X
5 | X
6 | X
7 | X
8 | X
9 | X
10 | X
Note on D5: SÄZÄN PowerCalc: Set automatically from the sheet tab by New Panelboard / Switchboard / MCC. To change it, use Rename Equipment (menu bar or Panel Tree) - that also renames the tab and every reference to this board.
Note on L6: SÄZÄN PowerCalc: Continuous load factor per NEC 210.19(A)(1) / 215.2(A)(1) / 215.3 - conductors and OCPD sized at 125% of continuous load. Commercial lighting is treated as continuous (3+ hours). Article 220 demand for general lighting is otherwise 100% in most occupancies.
Note on L7: SÄZÄN PowerCalc: Receptacle demand (NEC 220.44: first 10 kVA at 100%, remainder at 50%) is applied ONCE to this board's receptacles plus every receptacle load fed through it. This cell shows this section's share, so the combined total is never factored twice.
Note on E12: Corey McKinnon: SÄZÄN PowerCalc: Main/Bus rating override (A). Blank = calculated (next standard size at or above the demand amps, min 100 A). An override carries through to Horiz. Bus, the board's feeder (Feeder Schedule Req. Amp / OCPD / conductor) and the upstream transformer kVA. Shown red if below the calculated minimum.
Note on D13: SÄZÄN PowerCalc: Calculated: next standard AIC rating at or above the worst bus fault — study result (Short Circuit) or point-to-point estimate (H6), with a 14 kA minimum at 380 V and above (10 kA below). Turns red if the override is below the calculated minimum.
Note on E13: SÄZÄN PowerCalc: Override (optional): pick a series-rated or specified AIC if the design requires it. Clear to use the calculated value. Shaded amber when set, red if below the calculated minimum.
Note on G14: Corey McKinnon: SÄZÄN PowerCalc: Parallel conductor sets for this board's feeder. Taken from the Feeder Schedule when the board has a derived feeder (F-tag); otherwise estimated here with conductors capped at 750 kcmil per set (1/0 minimum in parallel).
Note on D19: SÄZÄN PowerCalc: Calculated: next standard bracing (UL 67/891) at or above the worst bus fault — study result (Short Circuit) or point-to-point estimate (H6). Shows — until fault data exists. Turns red if the override is below the calculated minimum.
Note on E19: SÄZÄN PowerCalc: Override (optional): pick a higher bracing if the spec requires it. Clear to use the calculated value.
Note on D20: SÄZÄN PowerCalc: Calculated: next standard bus rating at or above Main/Bus Rating (D12). Turns red if the override is below the calculated minimum.
Note on E20: SÄZÄN PowerCalc: Override (optional): pick a larger bus if the spec requires it. Clear to use the calculated value.
Note on J21: SÄZÄN PowerCalc: Managed by the Feed-Through command (rows 21–23). Locked: use the command to add, refresh or remove a downstream board.
Note on J24: SÄZÄN PowerCalc: Manual feed-through row: for equipment that does not have its own schedule. Enter a description and kVA.
Note on K24: SÄZÄN PowerCalc: Manual feed-through row: enter Description, Conn. kVA and Demand kVA. Its connected load is split evenly across the phases for the phase balance.

## TPL_MCC
[57 empty] | GEO_MAP |  | ANCHOR_TEXT | ANCHOR_COL | TARGET_COL | ROW_OFFSET | PILOT DEVICE LIST (dropdown source)
MOTOR CONTROL CENTER SCHEDULE | [56 empty] | NAME_CELL | D5 | MCC Tag / Name | C | D | 0 | None
Enter units in the CIRCUIT ENTRY DASHBOARD columns (O:W); starter / unit detail is in the STARTER & UNIT DETAIL block. Classification, breaker, wire size and VD% calculate automatically. | [56 empty] | NAME_OVR_CELL | - |  |  |  |  | H-O-A
| MCC INFORMATION |  |  |  | FAULT SUMMARY |  |  | LOAD SUMMARY & NEC 220 DEMAND | [48 empty] | VOLT_CELL | D8 | System Voltage | C | D | 0 | H-O-A, R/G Pilot
| MCC Tag / Name |  |  |  | Source Fault Avail. (A) |  |  | Category | Connected | Demand | [46 empty] | AIC_CELL | D13 | Std Device AIC (A) | C | D | 0 | H-O-A, R/G Pilot, Reset PB
| Fed From | Utility Service |  |  | Fault at Bus (A) |  |  | Lighting | 0 | 0 | [46 empty] | SRCFAULT_CELL | H5 | Source Fault Avail. (A) | G | H | 0 | Start/Stop PB, R/G Pilot
| Location |  |  |  | AIC Check | — |  | Receptacle | 0 | 0 | [46 empty] | BUSFAULT_CELL | H6 | Fault at Bus (A) | G | H | 0 | H-O-A, R/G Pilot, Ammeter
| System Voltage | [6 empty] | Motor | 0 | 0 | [46 empty] | DEMAND_CELL | H10 | Demand Total (kVA) | G | H | 0 | H-O-A, R/G Pilot, Ammeter, ETM
| V (L-L / L-N) |  |  |  | FEEDER SUMMARY |  |  | HVAC | 0 | 0 | [46 empty] | CONNECTED_CELL | K16 | TOTALS (kVA) | J | K | 0 | Per Vendor Submittal
| Phase / Wires |  |  |  | Demand Total (kVA) | 0 |  | Electric Heat | 0 | 0 | [46 empty] | ENG_VLL_CELL | BH31 | engine (do not delete) | BG | BH | 1
| Mains Type | MCB | Override |  | Demand FLA (A) |  |  | Kitchen Equip | 0 | 0 | [46 empty] | ENG_PH_CELL | BH33 | engine (do not delete) | BG | BH | 3
| Main/Bus Rating (A) |  |  |  | Feed |  |  | Continuous | 0 | 0 | [46 empty] | VD_RANGE | K33:K52
| Std Device AIC (A) | 10000 |  |  | Feeder Length (ft) |  |  | General | 0 | 0 | [46 empty] | CKT_FIRST | 33 | CKT | B |  | 1
| Mounting |  |  |  | Feeder Sets |  |  | Sub-Panels / Feed-Thru | 0 | 0 | [46 empty] | CKT_LAST | 52
| Enclosure |  |  |  | Feeder Conductor |  |  | Existing Load (NEC 220.87) | 0 | 0 | [46 empty] | CKT_PER_ROW | 1
| Manufacturer |  |  |  | Feeder OCPD (A) |  |  | TOTALS (kVA) | 0 | 0 | [46 empty] | CKT_DESC_COL | C
| Model / Series | [6 empty] | TOTALS (Amps) | [48 empty] | CKT_CLASS_COL | -
| Dims HxWxD (in) |  | Override |  | PHASE BALANCE | [51 empty] | CKT_QTY_COL | -
| Bus Bracing (kA) | — |  |  | Phase A (kVA) | 0 |  | FEED-THROUGH LOADS | [48 empty] | CKT_KVA_COL | AN | [5 empty] | FEED-THRU DETAIL (managed by Feed-Through — do not edit)
| Horiz. Bus Rating (A) | — |  |  | Phase B (kVA) | 0 |  | Description | Conn. kVA | Demand kVA | [46 empty] | CKT_POLES_COL | E | [5 empty] | Ph A kVA | Ph B kVA | Ph C kVA | Rcpt conn. kVA | Rcpt dem. kVA
| Wiring Class / Type |  |  |  | Phase C (kVA) | 0 | [48 empty] | VD — upstream cumulative %VD (from study) | 0% | FEEDTHRU_FIRST | 21 | Description | J |  | 1
[5 empty] | Imbalance % | 0% | [48 empty] | VD — branch %VD budget (5% less upstream) | 3% | FEEDTHRU_LAST | 23
[55 empty] | VD — combined worst-case %VD | 0% | FEEDTHRU_DESC_COL | J
[5 empty] | OL SIZING — NEC 430.32(A)(1) | [49 empty] | VD — combined status |  | PHASE_A_CELL | H19 | [5 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | Marked SF threshold | 1.15 |  | Subtotal (kVA): | 0 | 0 | [27 empty] | cls factor → | 1.25 | 1 | 1.25 | 1.25 | 1.25 | 1 | 1.25 | 1 | 1 | [7 empty] | engine (do not delete) | engine | PHASE_B_CELL | H20 | [5 empty] | 0 | 0 | 0 | 0 | 0
[5 empty] | OL trip — SF ≥ threshold | 125% | [50 empty] | PHASE_C_CELL | H21
[5 empty] | OL trip — SF < threshold | 115% | [50 empty] | REC_TOT_CELL | BH42
[5 empty] | Max per 430.32(C) | 140% | [50 empty] | REC_DEM_CELL | BH43
[5 empty] | OL trip = FLA × % above (see note) | [51 empty] | FT_CONN_COL | K
[57 empty] | FT_DETAIL_COL | BS
CIRCUIT SCHEDULE | [10 empty] | STARTER & UNIT DETAIL | [17 empty] | CIRCUIT ENTRY DASHBOARD | [27 empty] | BLOCK_SIZE | 20
CKT | Load Description |  | P | Bkr A | Classification | Conn. kVA | HP | Length Ft | VD % | Wire / Gnd | Starter Type | NEMA Size | Drive Type | Bypass | HOA | Service Factor | Motor FLA (A) | OL Setting (A) | OL Basis | Disconnect Type | Fuse / Frame (A) | Control Xfmr VA | Pilot Devices | Space Heater | Unit Space (X) | Section | Vert. Bus (A) | Notes | LTG | REC | MTR | HVC | HEAT | KIT | CONT | GEN | PNL | IsM | CtF | DmT | CktV | FLC | FLA | DesI | OCPDt | Pos | VA# | PhI | vaA | vaB | vaC | OVR | Cons | Sets |  |  | FT_SLOTS | 3
1 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | VD_COL | K
2 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 |  |  | CKT_NUM_COL | B
3 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 |  |  | FEEDTHRU_KVA_COL | L
4 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | CKT_BLOCK1_FIRST | 33
5 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | CKT_BLOCK1_LAST | 52
6 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | CKT_BLOCK2_FIRST | -
7 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | CKT_BLOCK2_LAST | -
8 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Bus bracing — calc. min (kA) |  | RESIZE_MODE | SINGLE
9 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | Horiz. bus — calc. min (A)
10 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Receptacle — total conn. incl. feed-thru (kVA) | 0
11 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Receptacle — combined demand (kVA) | 0
12 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | Feeder — parallel sets (750 kcmil max per set) | 0
13 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Std device AIC — calc. min (A) | 10000
14 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Main/Bus — calc. min (A)
15 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
16 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
17 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
18 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
19 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
20 |  |  |  |  | Space | [32 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
NOTES
1 | X
2 | X
3 | X
4 | X
5 | X
6 | X
7 | X
8 | X
9 | X
10 | X
Note on D5: SÄZÄN PowerCalc: Set automatically from the sheet tab by New Panelboard / Switchboard / MCC. To change it, use Rename Equipment (menu bar or Panel Tree) - that also renames the tab and every reference to this board.
Note on L6: SÄZÄN PowerCalc: Continuous load factor per NEC 210.19(A)(1) / 215.2(A)(1) / 215.3 - conductors and OCPD sized at 125% of continuous load. Commercial lighting is treated as continuous (3+ hours). Article 220 demand for general lighting is otherwise 100% in most occupancies.
Note on L7: SÄZÄN PowerCalc: Receptacle demand (NEC 220.44: first 10 kVA at 100%, remainder at 50%) is applied ONCE to this board's receptacles plus every receptacle load fed through it. This cell shows this section's share, so the combined total is never factored twice.
Note on E12: Corey McKinnon: SÄZÄN PowerCalc: Main/Bus rating override (A). Blank = calculated (next standard size at or above the demand amps, min 100 A). An override carries through to Horiz. Bus, the board's feeder (Feeder Schedule Req. Amp / OCPD / conductor) and the upstream transformer kVA. Shown red if below the calculated minimum.
Note on D13: SÄZÄN PowerCalc: Calculated: next standard AIC rating at or above the worst bus fault — study result (Short Circuit) or point-to-point estimate (H6), with a 14 kA minimum at 380 V and above (10 kA below). Turns red if the override is below the calculated minimum.
Note on E13: SÄZÄN PowerCalc: Override (optional): pick a series-rated or specified AIC if the design requires it. Clear to use the calculated value. Shaded amber when set, red if below the calculated minimum.
Note on G14: Corey McKinnon: SÄZÄN PowerCalc: Parallel conductor sets for this board's feeder. Taken from the Feeder Schedule when the board has a derived feeder (F-tag); otherwise estimated here with conductors capped at 750 kcmil per set (1/0 minimum in parallel).
Note on D19: SÄZÄN PowerCalc: Calculated: next standard bracing (UL 67/891) at or above the worst bus fault — study result (Short Circuit) or point-to-point estimate (H6). Shows — until fault data exists. Turns red if the override is below the calculated minimum.
Note on E19: SÄZÄN PowerCalc: Override (optional): pick a higher bracing if the spec requires it. Clear to use the calculated value.
Note on D20: SÄZÄN PowerCalc: Calculated: next standard bus rating at or above Main/Bus Rating (D12). Turns red if the override is below the calculated minimum.
Note on E20: SÄZÄN PowerCalc: Override (optional): pick a larger bus if the spec requires it. Clear to use the calculated value.
Note on J21: SÄZÄN PowerCalc: Managed by the Feed-Through command (rows 21–23). Locked: use the command to add, refresh or remove a downstream board.
Note on J24: SÄZÄN PowerCalc: Manual feed-through row: for equipment that does not have its own schedule. Enter a description and kVA.
Note on K24: SÄZÄN PowerCalc: Manual feed-through row: enter Description, Conn. kVA and Demand kVA. Its connected load is split evenly across the phases for the phase balance.
Note on G29: SÄZÄN PowerCalc: Nameplate SF per NEMA MG 1; OL trip = motor FLA × applicable percentage (NEC 430.32(A)(1)).

## TPL_Panelboard
[40 empty] | GEO_MAP |  | ANCHOR_TEXT | ANCHOR_COL | TARGET_COL | ROW_OFFSET
PANELBOARD SCHEDULE | [39 empty] | NAME_CELL | D5 | Panel Name | C | D | 0
[40 empty] | NAME_OVR_CELL | -
| PANEL INFORMATION |  |  |  | FAULT SUMMARY |  |  | LOAD SUMMARY & NEC 220 DEMAND | [31 empty] | VOLT_CELL | D8 | System Voltage | C | D | 0
| Panel Name |  |  |  | Source Fault Avail. (A) |  |  | Category | Connected | Demand | [29 empty] | AIC_CELL | D13 | Std Device AIC (A) | C | D | 0
| Fed From | Utility Service |  |  | Fault at Bus (A) |  |  | Lighting | 0 | 0 | [29 empty] | SRCFAULT_CELL | H5 | Source Fault Avail. (A) | G | H | 0
| Location |  |  |  | AIC Check | — |  | Receptacle | 0 | 0 | [29 empty] | BUSFAULT_CELL | H6 | Fault at Bus (A) | G | H | 0
| System Voltage | [6 empty] | Motor | 0 | 0 | [29 empty] | DEMAND_CELL | H10 | Demand Total (kVA) | G | H | 0
| V (L-L / L-N) |  |  |  | FEEDER SUMMARY |  |  | HVAC | 0 | 0 | [29 empty] | CONNECTED_CELL | K16 | TOTALS (kVA) | J | K | 0
| Phase / Wires |  |  |  | Demand Total (kVA) | 0 |  | Electric Heat | 0 | 0 | [29 empty] | ENG_VLL_CELL | AQ27 | engine (do not delete) | AP | AQ | 1
| Mains Type | MCB | Override |  | Demand FLA (A) |  |  | Kitchen Equip | 0 | 0 | [29 empty] | ENG_PH_CELL | AQ29 | engine (do not delete) | AP | AQ | 3
| Main/Bus Rating (A) |  |  |  | Feed |  |  | Continuous | 0 | 0 | [29 empty] | VD_RANGE | K29:K112
| Std Device AIC (A) | 10000 |  |  | Feeder Length (ft) |  |  | General | 0 | 0 | [29 empty] | CKT_FIRST | 29 | CKT | B |  | 1
| Mounting |  |  |  | Feeder Sets |  |  | Sub-Panels / Feed-Thru | 0 | 0 | [29 empty] | CKT_LAST | 112
| Enclosure |  |  |  | Feeder Conductor |  |  | Existing Load (NEC 220.87) | 0 | 0 | [29 empty] | CKT_PER_ROW | 1
| Manufacturer |  |  |  | Feeder OCPD (A) |  |  | TOTALS (kVA) | 0 | 0 | [29 empty] | CKT_DESC_COL | C
| Model / Series | [6 empty] | TOTALS (Amps) | [31 empty] | CKT_CLASS_COL | -
| Dims HxWxD (in) |  | Override |  | PHASE BALANCE | [34 empty] | CKT_QTY_COL | -
| Bus Bracing (kA) | — |  |  | Phase A (kVA) | 0 |  | FEED-THROUGH LOADS | [31 empty] | CKT_KVA_COL | W |  |  |  |  | FEED-THRU DETAIL (managed by Feed-Through — do not edit)
| Horiz. Bus Rating (A) | — |  |  | Phase B (kVA) | 0 |  | Description | Conn. kVA | Demand kVA | [29 empty] | CKT_POLES_COL | E |  |  |  |  | Ph A kVA | Ph B kVA | Ph C kVA | Rcpt conn. kVA | Rcpt dem. kVA
| Wiring Class / Type |  |  |  | Phase C (kVA) | 0 | [31 empty] | VD — upstream cumulative %VD (from study) | 0% | FEEDTHRU_FIRST | 21 | Description | J |  | 1
[5 empty] | Imbalance % | 0% | [31 empty] | VD — branch %VD budget (5% less upstream) | 3% | FEEDTHRU_LAST | 23
[38 empty] | VD — combined worst-case %VD | 0% | FEEDTHRU_DESC_COL | J
[38 empty] | VD — combined status |  | PHASE_A_CELL | H19 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[8 empty] | Subtotal (kVA): | 0 | 0 | [11 empty] | 1.25 | 1 | 1.25 | 1.25 | 1.25 | 1 | 1.25 | 1 | 1 | [7 empty] | engine (do not delete) | engine | PHASE_B_CELL | H20 |  |  |  |  | 0 | 0 | 0 | 0 | 0
[40 empty] | PHASE_C_CELL | H21
CIRCUIT SCHEDULE | [11 empty] | CIRCUIT ENTRY DASHBOARD | [27 empty] | REC_TOT_CELL | AQ38
CKT | Load Description |  | P | Bkr A | Classification | Conn. kVA | HP | Length Ft | VD % | Wire / Gnd | Notes | LTG | REC | MTR | HVC | HEAT | KIT | CONT | GEN | PNL | IsM | CtF | DmT | CktV | FLC | FLA | DesI | OCPDt | Pos | VA# | PhI | vaA | vaB | vaC | OVR | Cons | Sets |  |  | REC_DEM_CELL | AQ39
1 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | FT_CONN_COL | K
3 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 |  |  | FT_DETAIL_COL | AY
5 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 |  |  | BLOCK_SIZE | 42
7 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | FT_SLOTS | 3
9 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | VD_COL | K
11 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | CKT_NUM_COL | B
13 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | FEEDTHRU_KVA_COL | L
15 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Bus bracing — calc. min (kA) |  | CKT_BLOCK1_FIRST | 29
17 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | Horiz. bus — calc. min (A) |  | CKT_BLOCK1_LAST | 70
19 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Receptacle — total conn. incl. feed-thru (kVA) | 0 | CKT_BLOCK2_FIRST | 71
21 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Receptacle — combined demand (kVA) | 0 | CKT_BLOCK2_LAST | 112
23 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0 | Feeder — parallel sets (750 kcmil max per set) | 0 | RESIZE_MODE | TWOBLOCK
25 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Std device AIC — calc. min (A) | 10000
27 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | Main/Bus — calc. min (A)
29 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
31 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
33 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
35 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
37 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
39 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
41 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
43 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
45 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
47 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
49 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
51 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
53 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
55 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
57 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
59 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
61 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
63 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
65 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
67 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
69 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
71 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
73 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
75 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
77 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
79 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
81 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
83 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
2 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
4 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
6 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
8 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
10 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
12 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
14 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
16 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
18 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
20 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
22 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
24 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
26 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
28 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
30 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
32 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
34 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
36 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
38 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
40 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
42 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
44 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
46 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
48 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
50 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
52 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
54 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
56 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
58 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
60 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
62 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
64 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
66 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
68 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
70 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
72 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
74 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
76 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
78 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
80 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
82 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 | 0
84 |  |  |  |  | Space | [15 empty] | 0 | 0 | NONE |  | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 |  | 0 | 0
NOTES
1 | X
2 | X
3 | X
4 | X
5 | X
6 | X
7 | X
8 | X
9 | X
10 | X
Note on D5: SÄZÄN PowerCalc: Set automatically from the sheet tab by New Panelboard / Switchboard / MCC. To change it, use Rename Equipment (menu bar or Panel Tree) - that also renames the tab and every reference to this board.
Note on L6: SÄZÄN PowerCalc: Continuous load factor per NEC 210.19(A)(1) / 215.2(A)(1) / 215.3 - conductors and OCPD sized at 125% of continuous load. Commercial lighting is treated as continuous (3+ hours). Article 220 demand for general lighting is otherwise 100% in most occupancies.
Note on L7: SÄZÄN PowerCalc: Receptacle demand (NEC 220.44: first 10 kVA at 100%, remainder at 50%) is applied ONCE to this board's receptacles plus every receptacle load fed through it. This cell shows this section's share, so the combined total is never factored twice.
Note on E12: Corey McKinnon: SÄZÄN PowerCalc: Main/Bus rating override (A). Blank = calculated (next standard size at or above the demand amps, min 100 A). An override carries through to Horiz. Bus, the board's feeder (Feeder Schedule Req. Amp / OCPD / conductor) and the upstream transformer kVA. Shown red if below the calculated minimum.
Note on D13: SÄZÄN PowerCalc: Calculated: next standard AIC rating at or above the worst bus fault — study result (Short Circuit) or point-to-point estimate (H6), with a 14 kA minimum at 380 V and above (10 kA below). Turns red if the override is below the calculated minimum.
Note on E13: SÄZÄN PowerCalc: Override (optional): pick a series-rated or specified AIC if the design requires it. Clear to use the calculated value. Shaded amber when set, red if below the calculated minimum.
Note on G14: Corey McKinnon: SÄZÄN PowerCalc: Parallel conductor sets for this board's feeder. Taken from the Feeder Schedule when the board has a derived feeder (F-tag); otherwise estimated here with conductors capped at 750 kcmil per set (1/0 minimum in parallel).
Note on D19: SÄZÄN PowerCalc: Calculated: next standard bracing (UL 67/891) at or above the worst bus fault — study result (Short Circuit) or point-to-point estimate (H6). Shows — until fault data exists. Turns red if the override is below the calculated minimum.
Note on E19: SÄZÄN PowerCalc: Override (optional): pick a higher bracing if the spec requires it. Clear to use the calculated value.
Note on D20: SÄZÄN PowerCalc: Calculated: next standard bus rating at or above Main/Bus Rating (D12). Turns red if the override is below the calculated minimum.
Note on E20: SÄZÄN PowerCalc: Override (optional): pick a larger bus if the spec requires it. Clear to use the calculated value.
Note on J21: SÄZÄN PowerCalc: Managed by the Feed-Through command (rows 21–23). Locked: use the command to add, refresh or remove a downstream board.
Note on J24: SÄZÄN PowerCalc: Manual feed-through row: for equipment that does not have its own schedule. Enter a description and kVA.
Note on K24: SÄZÄN PowerCalc: Manual feed-through row: enter Description, Conn. kVA and Demand kVA. Its connected load is split evenly across the phases for the phase balance.

## NEC_Data
NEC REFERENCE DATA | [65 empty] | TRANSFORMER CONFIG — system voltages (referenced by the Transformer Schedule) |  |  |  |  | TRANSFORMER DEFAULTS | [16 empty] | NEC CODE-REFERENCE MAP - every edition-aware citation in the workbook reads this table through NECREF(). Key = 2023 number. Blank cell = same as key.
⚠ Reference tables only. Verify against your adopted NEC edition and manufacturer data. A licensed PE must approve all results. | [72 empty] | SÄZÄN STANDARD FEEDER SCHEDULE — COPPER, 3-PHASE (code + N = with neutral) |  |  |  |  | SÄZÄN STANDARD FEEDER SCHEDULE — COPPER, 1-PHASE (code + N = with neutral) |  |  |  |  | SÄZÄN STANDARD FEEDER SCHEDULE — ALUMINIUM, 3-PHASE (code + N = with neutral; starts at 100A) |  |  |  |  | Key (2023) | NEC 2020 | NEC 2023 | NEC 2026 | Basis / status
[66 empty] | System Voltage | Base V | Ph | Typical Conn | L-N V | Type / Rise | Dry-type, 150°C rise | Code | Sets | Conduit Size | Conductors | Ground | Code | Sets | Conduit Size | Conductors | Ground | Code | Sets | Conduit Size | Conductors | Ground | 110.9 | 110.9 | 110.9 | 110.9 | Same number in 2020 / 2023 / 2026 per published summaries - verify | Source: NEMA PB 1 / UL 67 & UL 891 standard bus ampacities; UL 67/891 short-circuit (bracing) ratings. Used by Horiz. Bus Rating and Bus Bracing on panel schedules. |  | Source: UL 1008 transfer-switch frame ratings (common manufacturer sizes). WCR values are typical 'any breaker' withstand ratings - always verify against the specific manufacturer / protective device. Used by Generator > Transfer Switches.
A. SYSTEM VOLTAGES | [6 empty] | B. STD OCPD (240.6) |  | C. CONDUCTORS (310.16 ampacity ¦ Ch.9 circular mils ¦ Bussmann C-values) | [11 empty] | D. EGC (250.122) |  |  |  | E. VD CONSTANTS |  |  | F. NEMA RECEPTACLES (by system voltage) — reference only; verify with PE | [8 empty] | NEC 220.42 — GENERAL LIGHTING DEMAND BY OCCUPANCY | [7 empty] | NEC 310.16 — CONDUCTOR AMPACITY (75°C) |  |  |  | NEC 250.122 — EQUIP GROUNDING CONDUCTOR |  |  | NEC 250.66 / 250.102(C)(1) — GEC & BONDING JUMPER |  |  |  | TYPICAL TRANSFORMER X/R (LV DRY-TYPE, IEEE 141) |  | TRANSFORMER SCHEDULE PICKLISTS | [7 empty] | 480Y/277V 3Ø 4W | 480 | 3 | Delta | 277 | Taps | 6 x 2.5% FCBN, 2 x 2.5% FCAN | 20 | 1 | 3/4" | 3 #12 | #12 | 20 | 1 | 3/4" | 2 #12 | #12 | 100 | 1 | 1-1/4" | 3 #1 | #6 | 110.10 | 110.10 | 110.10 | 110.10 | Same number in 2020 / 2023 / 2026 per published summaries - verify | STD BUS RATINGS | STD BUS BRACING | STD ATS RATINGS | TYP. ATS WCR
System | Nominal V (L-L) | Phase | Wires | V (L-N) | Class |  | Amps |  | Size (AWG/kcmil) | Circular Mils | Cu 60°C | Cu 75°C | Cu 90°C | Al 60°C | Al 75°C | Al 90°C | C (Cu-steel) | C (Al-steel) | C (Cu-nonmag) | C (Al-nonmag) | OCPD ≤ (A) | Cu | Al |  | Constant | Value |  | 120 V | 208 V | 240 V | 277 V | 480 V | 600 V | Disc Frame (A) | Disc NEMA Encl | Supplied By | Occupancy | 1st (VA) | DF1 | 2nd (VA) | DF2 | DF3 (rem) | Conn kVA (retired) | Demand kVA (retired) | Size | Cu (A) | Al (A) | CM | OCPD (A) | Cu EGC | Al EGC | Max CM | Phase Size | Cu | Al | kVA | X/R typ | Ph | Pri V | Sec V | Pri Conn | Sec Conn | Type / Rise | Taps | Enclosure | 208Y/120V 3Ø 4W | 208 | 3 | Wye | 120 | Enclosure | NEMA 1 | 30 | 1 | 3/4" | 3 #10 | #10 | 30 | 1 | 3/4" | 2 #10 | #10 | 100N | 1 | 1-1/4" | 4 #1 | #6 | 110.14 | 110.14 | 110.14 | 110.14 | Same number in 2020 / 2023 / 2026 per published summaries - verify | Amps | kA | Amps | A (verify)
120V 1Ø 2W | 120 | 1 | 2 | 120 | LV |  | 15 |  | 14 | 4110 | 15 | 20 | 25 |  |  |  | 389 | 237 | 389 | 237 | 15 | 14 | 12 |  | K – Copper (cmil·Ω/ft) | 12.9 |  | 1-15R | 6-15R | 2-20R | 7-15R | L8-20R | L9-20R | 30 | 1 | Electrical | Commercial / Other | 1000000000000 | 100% | 1000000000000 | 100% | 100% |  |  | 14 | 20 |  | 4110 | 15 | 14 | 12 | 66360 | 2 or smaller | 8 | 6 | 15 | 1.5 | 1 | 208 | 120 | Δ | Y — XO gnd | Dry, 150°C rise | ±2×2.5% FCBN | NEMA 1, indoor | 480V 3Ø 3W | 480 | 3 | Delta | 277 | %Z (default) | 5.75 | 40 | 1 | 1" | 3 #8 | #10 | 40 | 1 | 1" | 2 #8 | #10 | 125 | 1 | 1-1/2" | 3 #2/0 | #4 | 110.24 | 110.24 | 110.24 | 110.24 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 100 | 10 | 30 | 10000
120/240V 1Ø 3W | 240 | 1 | 3 | 120 | LV |  | 20 |  | 12 | 6530 | 20 | 25 | 30 | 15 | 20 | 25 | 617 | 376 | 617 | 376 | 20 | 12 | 10 |  | K – Aluminum (cmil·Ω/ft) | 21.2 |  | 5-15R | 6-20R | 2-30R | 7-20R | L12-20R | L13-20R | 60 | 3R | Mechanical | Warehouse / Storage | 12500 | 100% | 1000000000000 | 50% | 50% |  |  | 12 | 25 | 20 | 6530 | 20 | 12 | 10 | 105600 | 1 or 1/0 | 6 | 4 | 30 | 2 | 3 | 240 | 208 | Y | Y — XO ungrnd | Dry, 115°C rise | ±4×2.5% FCBN | NEMA 2, indoor drip | 240V 3Ø 3W | 240 | 3 | Delta | 139 | Source X/R (default) | 15 | 50 | 1 | 1" | 3 #6 | #10 | 50 | 1 | 1" | 2 #6 | #10 | 125N | 1 | 1-1/2" | 4 #2/0 | #4 | 210.19 | 210.19 | 210.19 | 210.19 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 125 | 14 | 40 | 10000
208Y/120V 3Ø 4W | 208 | 3 | 4 | 120 | LV |  | 25 |  | 10 | 10380 | 30 | 35 | 40 | 25 | 30 | 35 | 981 | 599 | 982 | 599 | 60 | 10 | 8 |  | VD limit – branch (recommended) | 3% |  | 5-20R | 6-30R | 6-15R | 7-30R | L12-30R | L13-30R | 100 | 4 |  | Hospital | 50000 | 40% | 1000000000000 | 20% | 20% |  |  | 10 | 35 | 30 | 10380 | 60 | 10 | 8 | 167800 | 2/0 or 3/0 | 4 | 2 | 45 | 2.2 |  | 480 | 240 |  | Δ | Dry, 80°C rise | 6×2.5% FCAN + 2×2.5% FCBN | NEMA 3R, outdoor | 240/120V 1Ø 3W | 240 | 1 | Delta | 120 | Inrush ×FLA | 10 | 60 | 1 | 1-1/4" | 3 #4 | #10 | 60 | 1 | 1-1/4" | 2 #4 | #10 | 150 | 1 | 2" | 3 #3/0 | #4 | 210.20 | 210.20 | 210.20 | 210.20 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 150 | 18 | 70 | 22000
240V 3Ø 3W (Delta) | 240 | 3 | 3 |  | LV |  | 30 |  | 8 | 16510 | 40 | 50 | 55 | 35 | 40 | 45 | 1557 | 951 | 1559 | 952 | 100 | 8 | 6 |  | VD limit – total (recommended) — linked to Cfg_VDTotal | 5% |  | 5-30R | 6-50R | 6-20R | 7-50R | L16-20R | L17-20R | 200 | 4X |  | Hotel / Motel | 20000 | 50% | 100000 | 40% | 30% |  |  | 8 | 50 | 40 | 16510 | 100 | 8 | 6 | 350000 | over 3/0 thru 350 | 2 | 1/0 | 75 | 2.6 |  | 600 | 480 |  | Δ — corner gnd | Cast coil, 150°C rise | None | NEMA 4X, washdown | 208V 3Ø 3W | 208 | 3 | Delta | 120 |  |  | 70 | 1 | 1-1/4" | 3 #4 | #8 | 70 | 1 | 1-1/4" | 2 #4 | #8 | 150N | 1 | 2" | 4 #3/0 | #4 | 215.2 | 215.2 | 215.2 | 215.2 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 225 | 22 | 100 | 22000
240V 3Ø 4W (High-Leg) | 240 | 3 | 4 | 120 | LV |  | 35 |  | 6 | 26240 | 55 | 65 | 75 | 40 | 50 | 60 | 2425 | 1481 | 2430 | 1482 | 200 | 6 | 4 |  | √3 (3Ø factor) | 1.732 |  | 5-50R | L6-15R | 6-30R | L7-15R | L16-30R | L17-30R | 400 | 7 |  | Dwelling | 3000 | 100% | 120000 | 35% | 25% |  |  | 6 | 65 | 50 | 26240 | 200 | 6 | 4 | 600000 | over 350 thru 600 | 1/0 | 3/0 | 112.5 | 3 |  | 2400 | 600 |  |  | Liquid-filled, 65°C rise |  | NEMA 12, industrial | 600Y/347V 3Ø 4W | 600 | 3 | Delta | 347 | Max nodes (capacity) | 250 | 80 | 1 | 1-1/4" | 3 #2 | #8 | 80 | 1 | 1-1/4" | 2 #2 | #8 | 175 | 1 | 2" | 3 #4/0 | #4 | 215.3 | 215.3 | 215.3 | 215.3 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 250 | 25 | 150 | 22000
480Y/277V 3Ø 4W | 480 | 3 | 4 | 277 | LV |  | 40 |  | 4 | 41740 | 70 | 85 | 95 | 55 | 65 | 75 | 3806 | 2346 | 3826 | 2350 | 300 | 4 | 2 |  |  |  |  | L1-15R | L6-20R | 6-50R | L7-20R | L19-20R | L20-20R | 600 | 9 |  | NEC 220.42 demand factors are NOT applied — lighting demand = 100% of connected (project decision). Threshold/DF data retained for reference. | [7 empty] | 4 | 85 | 65 | 41740 | 300 | 4 | 2 | 1100000 | over 600 thru 1100 | 2/0 | 4/0 | 150 | 3.2 |  | 4160 |  |  |  | K-4 dry, 150°C rise |  | Ventilated, indoor | [7 empty] | 90 | 1 | 1-1/4" | 3 #2 | #8 | 90 | 1 | 1-1/4" | 2 #2 | #8 | 175N | 1 | 2" | 4 #4/0 | #4 | 220 | 220 | 220 | 120 | 2026: Art. 220 renumbered to Art. 120, suffix kept (published 2026 summaries) - verify against NFPA 70-2026 | 400 | 35 | 200 | 22000
480V 3Ø 3W | 480 | 3 | 3 |  | LV |  | 45 |  | 3 | 52620 | 85 | 100 | 110 | 65 | 75 | 85 | 4774 | 2952 | 4811 | 2961 | 400 | 3 | 1 |  | F. TERMINATION & MIN-SIZE RULES — NEC 110.14(C) |  |  | L5-15R | L6-30R | L2-20R | L7-30R | L19-30R | L20-30R | 800 | 12 |  | NEC 220.44 — RECEPTACLE / GENERAL POWER DEMAND | [7 empty] | 3 | 100 | 75 | 52620 | 400 | 3 | 1 | 99999999 | over 1100 | 3/0 | 250 | 225 | 3.6 |  | 12470 |  |  |  | K-13 dry, 150°C rise | [7 empty] | Motor contribution ×FLA | 4 | 100 | 1 | 1-1/2" | 3 #1 | #8 | 100 | 1 | 1-1/2" | 2 #1 | #8 | 200 | 1 | 2" | 3 #250 | #4 | 220.12 | 220.12 | 220.12 | 120.12 | VERIFY - summaries conflict for 2026 (120.12 vs 120.13); 2023 also split dwelling lighting into 220.41 | 600 | 42 | 225 | 30000
600Y/347V 3Ø 4W | 600 | 3 | 4 | 347 | LV |  | 50 |  | 2 | 66360 | 95 | 115 | 130 | 75 | 90 | 100 | 5907 | 3713 | 6044 | 3730 | 500 | 2 | 1/0 |  | Branch amp col ≤100 A (60°C) | 3 |  | L5-20R | 11-15R | L6-15R |  | L22-20R | L23-20R | 1200 |  |  | First (VA) @ 100% | 10000 | [6 empty] | 2 | 115 | 90 | 66360 | 500 | 2 | 1/0 | SBJ over 1100 kcmil: 12.5% of largest ungrounded phase area per 250.28(D)(1). |  |  |  | 300 | 4 |  | 13200 | [11 empty] | MCC motor ×FLA | 5 | 125 | 1 | 1-1/2" | 3 #1 | #6 | 125 | 1 | 1-1/2" | 2 #1 | #6 | 200N | 1 | 2-1/2" | 4 #250 | #4 | 220.14 | 220.14 | 220.14 | 120.14 | 2026: Art. 220 renumbered to Art. 120, suffix kept (published 2026 summaries) - verify against NFPA 70-2026 | 800 | 50 | 260 | 42000
600V 3Ø 3W | 600 | 3 | 3 |  | LV |  | 60 |  | 1 | 83690 | 110 | 130 | 150 | 85 | 100 | 115 | 7293 | 4645 | 7493 | 4678 | 600 | 1 | 2/0 |  | Feeder amp col ≤100 A (60°C) | 3 |  | L5-30R | 11-20R | L6-20R |  | L22-30R | L23-30R |  |  |  | Remainder demand factor | 50% | [6 empty] | 1 | 130 | 100 | 83690 | 600 | 1 | 2/0 |  |  |  |  | 500 | 4.5 |  | 13800 | [13 empty] | 150 | 1 | 2" | 3 #1/0 | #6 | 150 | 1 | 2" | 2 #1/0 | #6 | 225 | 1 | 2-1/2" | 3 #300 | #2 | 220.42 | 220.42 | 220.42 | 120.42 | 2026: Art. 220 renumbered to Art. 120, suffix kept (published 2026 summaries) - verify against NFPA 70-2026 | 1000 | 65 | 400 | 42000
2400V 3Ø 3W | 2400 | 3 | 3 |  | MV |  | 70 |  | 1/0 | 105600 | 125 | 150 | 170 | 100 | 120 | 135 | 8925 | 5777 | 9317 | 5838 | 800 | 1/0 | 3/0 |  | Min conductor position (2 = #12) | 2 |  | L5-50R | 11-30R | L6-30R | [14 empty] | 1/0 | 150 | 120 | 105600 | 800 | 1/0 | 3/0 |  |  |  |  | 750 | 5 | [13 empty] | Feeder %VD limit | 3% | 175 | 1 | 2" | 3 #2/0 | #6 | 175 | 1 | 2" | 2 #2/0 | #6 | 225N | 1 | 2-1/2" | 4 #300 | #2 | 220.44 | 220.44 | 220.44 | 120.44 | 2026: Art. 220 renumbered to Art. 120, suffix kept (published 2026 summaries) - verify against NFPA 70-2026 | 1200 | 85 | 600 | 50000
4160Y/2400V 3Ø 4W | 4160 | 3 | 4 | 2400 | MV |  | 80 |  | 2/0 | 133100 | 145 | 175 | 195 | 115 | 135 | 150 | 10755 | 7187 | 11424 | 7301 | 1000 | 2/0 | 4/0 |  |  |  |  | TT-30R | 11-50R | 10-30R | [14 empty] | 2/0 | 175 | 135 | 133100 | 1000 | 2/0 | 4/0 |  |  |  |  | 1000 | 5.5 | [13 empty] | Total %VD limit | 5% | 200 | 1 | 2" | 3 #3/0 | #6 | 200 | 1 | 2" | 2 #3/0 | #6 | 250 | 1 | 3" | 3 #350 | #2 | 220.56 | 220.56 | 220.56 | 120.56 | 2026: Art. 220 renumbered to Art. 120, suffix kept (published 2026 summaries) - verify against NFPA 70-2026 | 1600 | 100 | 800 | 50000
4160V 3Ø 3W | 4160 | 3 | 3 |  | MV |  | 90 |  | 3/0 | 167800 | 165 | 200 | 225 | 130 | 155 | 175 | 12844 | 8826 | 13923 | 9110 | 1200 | 3/0 | 250 | [5 empty] | L11-15R | 10-50R | [14 empty] | 3/0 | 200 | 155 | 167800 | 1200 | 3/0 | 250 |  |  |  |  | 1500 | 6 | [15 empty] | 225 | 1 | 2" | 3 #4/0 | #4 | 225 | 1 | 2" | 2 #4/0 | #4 | 250N | 1 | 3" | 4 #350 | #2 | 220.87 | 220.87 | 220.87 | 120.87 | 2026 120.87: measured demand x125% + new load MINUS removed load (Load Calc C38 used only when 2026 selected) | 2000 | 125 | 1000 | 65000
4800V 3Ø 3W | 4800 | 3 | 3 |  | MV |  | 100 |  | 4/0 | 211600 | 195 | 230 | 260 | 150 | 180 | 205 | 15082 | 10741 | 16673 | 11174 | 1600 | 4/0 | 350 | [5 empty] | L11-20R | 14-20R | [14 empty] | 4/0 | 230 | 180 | 211600 | 1600 | 4/0 | 350 |  |  |  |  | 2000 | 6.5 | [15 empty] | 250 | 1 | 2-1/2" | 3 #250 | #4 | 250 | 1 | 2-1/2" | 2 #250 | #4 | 300 | 1 | 3" | 3 #500 | #2 | 230.2 | 230.2 | 230.2 | 230.2 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 2500 | 150 | 1200 | 65000
6900V 3Ø 3W | 6900 | 3 | 3 |  | MV |  | 110 |  | 250 | 250000 | 215 | 255 | 290 | 170 | 205 | 230 | 16483 | 12122 | 18594 | 12862 | 2000 | 250 | 400 | [5 empty] | L11-30R | 14-30R | [14 empty] | 250 | 255 | 205 | 250000 | 2000 | 250 | 400 |  |  |  |  | 2500 | 7 | [15 empty] | 300 | 1 | 3" | 3 #350 | #4 | 300 | 1 | 3" | 2 #350 | #4 | 300N | 1 | 3-1/2" | 4 #500 | #2 | 240.4 | 240.4 | 240.4 | 240.4 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 3000 | 200 | 1600 | 85000
12470Y/7200V 3Ø 4W | 12470 | 3 | 4 | 7200 | MV |  | 125 |  | 300 | 300000 | 240 | 285 | 320 | 195 | 230 | 260 | 18177 | 13910 | 20868 | 14923 | 2500 | 350 | 600 | [5 empty] | 15-15R | 14-50R | [14 empty] | 300 | 285 | 230 | 300000 | 2500 | 350 | 600 |  |  |  |  | Fallback only — X/R is calculated from load losses when they are entered. | [16 empty] | 350 | 1 | 3" | 3 #500 | #2 | 350 | 1 | 3" | 2 #500 | #2 | 350 | 2 | 2" | 3 #4/0 | #2 | 240.6 | 240.6 | 240.6 | 240.6 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 4000 |  | 2000 | 100000
13200V 3Ø 3W | 13200 | 3 | 3 |  | MV |  | 150 |  | 350 | 350000 | 260 | 310 | 350 | 210 | 250 | 280 | 19704 | 15484 | 22737 | 16813 | 3000 | 400 | 600 | [5 empty] | 15-20R | 14-60R | [14 empty] | 350 | 310 | 250 | 350000 | 3000 | 400 | 600 | [21 empty] | 380 | 1 | 3" | 3 #500 | #2 | 380 | 1 | 3" | 2 #500 | #2 | 350N | 2 | 2" | 4 #4/0 | #2 | 250.28 | 250.28 | 250.28 | 250.28 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 5000 |  | 2500 | 100000
13800V 3Ø 3W | 13800 | 3 | 3 |  | MV |  | 175 |  | 400 | 400000 | 280 | 335 | 380 | 225 | 270 | 305 | 20566 | 16671 | 24297 | 18506 | 4000 | 500 | 750 | [5 empty] | 15-30R | L14-20R | [14 empty] | 400 | 335 | 270 | 400000 | 4000 | 500 | 750 | [21 empty] | 400 | 2 | 2" | 3 #3/0 | #2 | 400 | 2 | 2" | 2 #3/0 | #2 | 400 | 2 | 2" | 3 #250 | #1 | 250.66 | 250.66 | 250.66 | 250.66 | Same number in 2020 / 2023 / 2026 per published summaries - verify | 6000 |  | 3000 | 100000
24940Y/14400V 3Ø 4W | 24940 | 3 | 4 | 14400 | MV |  | 200 |  | 500 | 500000 | 320 | 380 | 430 | 260 | 310 | 350 | 22185 | 18756 | 26706 | 21391 | 5000 | 700 | 1200 | [5 empty] | 15-50R | L14-30R | [14 empty] | 500 | 380 | 310 | 500000 | [24 empty] | 500 | 2 | 2-1/2" | 3 #250 | #2 | 20N | 1 | 3/4" | 3 #12 | #12 | 400N | 2 | 2-1/2" | 4 #250 | #1 | 250.102 | 250.102 | 250.102 | 250.102 | Same number in 2020 / 2023 / 2026 per published summaries - verify |  |  | 4000 | 100000
34500V 3Ø 3W | 34500 | 3 | 3 |  | MV |  | 225 |  | 600 | 600000 | 350 | 420 | 475 | 285 | 340 | 385 | 22965 | 20093 | 28033 | 23451 | 6000 | 800 | 1200 | [5 empty] | 15-60R | L14-60R | [14 empty] | 600 | 420 | 340 | 600000 | [24 empty] | 600 | 2 | 3" | 3 #350 | #1 | 30N | 1 | 3/4" | 3 #10 | #10 | 500 | 2 | 2-1/2" | 3 #350 | #1/0 | 250.122 | 250.122 | 250.122 | 250.122 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 250 |  | 700 | 700000 | 385 | 460 | 520 | 315 | 375 | 425 | 23746.3333 | 21208.3333 | 29167.6667 | 25134.3333 | [8 empty] | L15-20R | [15 empty] | 750 | 475 | 385 | 750000 | [24 empty] | 700 | 2 | 3" | 3 #500 | #1/0 | 40N | 1 | 1" | 3 #8 | #10 | 500N | 2 | 3" | 4 #350 | #1/0 | 310.16 | 310.16 | 310.16 | 310.16 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 300 |  | 750 | 750000 | 400 | 475 | 535 | 320 | 385 | 435 | 24137 | 21766 | 29735 | 25976 | [8 empty] | L15-30R | [43 empty] | 760 | 2 | 3" | 3 #500 | #1/0 | 50N | 1 | 1" | 3 #6 | #10 | 600 | 2 | 3" | 3 #500 | #2/0 | 430.24 | 430.24 | 430.24 | 430.24 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 350 |  | 800 | 800000 | 410 | 490 | 555 | 330 | 395 | 445 | 24365.2 | 22108.4 | 30086.2 | 26536.6 | [8 empty] | L21-20R | [43 empty] | 800 | 3 | 3" | 3 #300 | #1/0 | 60N | 1 | 1-1/4" | 3 #4 | #10 | 600N | 2 | 3" | 4 #500 | #2/0 | 430.32 | 430.32 | 430.32 | 430.32 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 400 |  | 1000 | 1000000 | 455 | 545 | 615 | 375 | 445 | 500 | 25278 | 23478 | 31491 | 28779 | [8 empty] | L21-30R | [43 empty] | 1000 | 3 | 3" | 3 #400 | #2/0 | 70N | 1 | 1-1/4" | 3 #4 | #8 | 700 | 3 | 3" | 3 #350 | #3/0 | 430.248 | 430.248 | 430.248 | 430.248 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 450 | [65 empty] | 1200 | 4 | 3" | 3 #350 | #3/0 | 80N | 1 | 1-1/4" | 3 #2 | #8 | 700N | 3 | 3" | 4 #350 | #3/0 | 430.250 | 430.250 | 430.250 | 430.250 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 500 |  | Raceway magnetic classification — selects the Bussmann Table 4 column pair | [63 empty] | 1600 | 5 | 3" | 3 #400 | #4/0 | 90N | 1 | 1-1/4" | 3 #2 | #8 | 800 | 3 | 3" | 3 #400 | #3/0 | 450 | 450 | 450 | 450 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 600 |  | Raceway | Magnetic? | [62 empty] | 2000 | 6 | 3" | 3 #400 | #250 | 100N | 1 | 1-1/2" | 3 #1 | #8 | 800N | 3 | 3" | 4 #400 | #3/0 | 450.3 | 450.3 | 450.3 | 450.3 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 700 |  | Steel | Y | [62 empty] | 2500 | 7 | 3" | 3 #500 | #350 | 125N | 1 | 1-1/2" | 3 #1 | #6 | 1000 | 4 | 3" | 3 #350 | #4/0 | 620.14 | 620.14 | 620.14 | 620.14 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 800 |  | PVC | N | [62 empty] | 3000 | 8 | 3" | 3 #500 | #400 | 150N | 1 | 2" | 3 #1/0 | #6 | 1000N | 4 | 3" | 4 #350 | #4/0 | 625 | 625 | 625 | 625 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 1000 |  | Aluminum | N | [62 empty] | 3500 | 10 | 3" | 3 #500 | #400 | 175N | 1 | 2" | 3 #2/0 | #6 | 1200 | 4 | 3" | 3 #500 | #250 | 700 | 700 | 700 | 700 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 1200 | [65 empty] | 4000 | 11 | 3" | 3 #500 | #500 | 200N | 1 | 2" | 3 #3/0 | #6 | 1200N | 4 | 3-1/2" | 4 #500 | #250 | 230.42 | 230.42 | 230.42 | 230.42 | Same number in 2020 / 2023 / 2026 per published summaries - verify
[7 empty] | 1600 | [65 empty] | 20N | 1 | 3/4" | 4 #12 | #12 | 225N | 1 | 2" | 3 #4/0 | #4 | 1600 | 6 | 3" | 3 #400 | #350
[7 empty] | 2000 | [65 empty] | 30N | 1 | 3/4" | 4 #10 | #10 | 250N | 1 | 2-1/2" | 3 #250 | #4 | 1600N | 6 | 3" | 4 #400 | #350
[7 empty] | 2500 | [65 empty] | 40N | 1 | 1" | 4 #8 | #10 | 300N | 1 | 3" | 3 #350 | #4 | 2000 | 7 | 3" | 3 #500 | #400
[7 empty] | 3000 | [65 empty] | 50N | 1 | 1" | 4 #6 | #10 | 350N | 1 | 3" | 3 #500 | #2 | 2000N | 7 | 3-1/2" | 4 #500 | #400
[7 empty] | 4000 | [65 empty] | 60N | 1 | 1-1/4" | 4 #4 | #10 | 380N | 1 | 3" | 3 #500 | #2 | 2500 | 9 | 3" | 3 #500 | #600
[7 empty] | 5000 | [65 empty] | 70N | 1 | 1-1/4" | 4 #4 | #8 | 400N | 2 | 2" | 3 #3/0 | #2 | 2500N | 9 | 3-1/2" | 4 #500 | #600
[7 empty] | 6000 | [65 empty] | 80N | 1 | 1-1/2" | 4 #2 | #8 | EXIST | EXISTING FEEDER TO REMAIN |  |  |  | 3000 | 10 | 3" | 3 #500 | #600
[73 empty] | 90N | 1 | 1-1/2" | 4 #2 | #8 | [5 empty] | 3000N | 10 | 3-1/2" | 4 #500 | #600
F. MOTOR FLC — THREE-PHASE (NEC 430.250) [amps] | [5 empty] | G. MOTOR FLC — 1Ø (430.248) |  |  |  | H. LOAD CLASSIFICATION | [14 empty] | N. STD GENERATOR kW |  | O. STD UPS kVA | [45 empty] | 100N | 1 | 1-1/2" | 4 #1 | #8 | [5 empty] | 3500 | 10 | 3" | 3 #500 | #600
HP | 208V | 230V | 460V | 575V |  | HP | 115V | 230V |  | Classification | Cont. Factor | Is Motor | DemType |  | I. KITCHEN 220.56 |  |  | J. XFMR kVA 3Ø |  |  | K. XFMR kVA 1Ø |  | L. STD AIC (A) | Xfmr %Z default = 5.75 — verify w/ mfr | 30 |  | 10 | [45 empty] | 125N | 1 | 1-1/2" | 4 #1 | #6 | [5 empty] | 3500N | 10 | 3-1/2" | 4 #500 | #600
0.5 | 2.4 | 2.2 | 1.1 | 0.9 |  | 0.5 | 9.8 | 4.9 |  | Receptacle | 1 | 0 | REC |  | Units ≥ | Factor |  | 15 |  |  | 15 |  | 10000 |  | 40 |  | 15 | [45 empty] | 150N | 1 | 2" | 4 #1/0 | #6 | [5 empty] | 4000 | 10 | 3" | 3 #500 | #750
0.75 | 3.5 | 3.2 | 1.6 | 1.3 |  | 0.75 | 13.8 | 6.9 |  | Lighting | 1.25 | 0 | LTG |  | 0 | 1 |  | 30 |  |  | 25 |  | 14000 |  | 50 |  | 20 | [45 empty] | 175N | 1 | 2" | 4 #2/0 | #6 | [5 empty] | 4000N | 10 | 3-1/2" | 4 #500 | #750
1 | 4.6 | 4.2 | 2.1 | 1.7 |  | 1 | 16 | 8 |  | Motor | 1.25 | 1 | MTR |  | 3 | 0.9 |  | 45 |  |  | 37.5 |  | 18000 |  | 60 |  | 30 | [45 empty] | 200N | 1 | 2" | 4 #3/0 | #6 | [5 empty] | EXIST | EXISTING FEEDER TO REMAIN
1.5 | 6.6 | 6 | 3 | 2.4 |  | 1.5 | 20 | 10 |  | HVAC | 1.25 | 0 | HVC |  | 4 | 0.8 |  | 75 |  |  | 50 |  | 22000 |  | 80 |  | 40 | [45 empty] | 225N | 1 | 2-1/2" | 4 #4/0 | #4
2 | 7.5 | 6.8 | 3.4 | 2.7 |  | 2 | 24 | 12 |  | Electric Heat | 1.25 | 0 | HEAT |  | 5 | 0.7 |  | 112.5 |  |  | 75 |  | 25000 |  | 100 |  | 50 | [45 empty] | 250N | 1 | 3" | 4 #250 | #4
3 | 10.6 | 9.6 | 4.8 | 3.9 |  | 3 | 34 | 17 |  | Kitchen Equip | 1 | 0 | KIT |  | 6 | 0.65 |  | 150 |  |  | 100 |  | 35000 |  | 125 |  | 60 | [45 empty] | 300N | 1 | 3" | 4 #350 | #4
5 | 16.7 | 15.2 | 7.6 | 6.1 |  | 5 | 56 | 28 |  | Continuous (Other) | 1.25 | 0 | CONT |  |  |  |  | 225 |  |  | 167 |  | 42000 |  | 150 |  | 80 | [45 empty] | 350N | 1 | 3-1/2" | 4 #500 | #2
7.5 | 24.2 | 22 | 11 | 9 |  | 7.5 | 80 | 40 |  | Non-Continuous | 1 | 0 | GEN |  |  |  |  | 300 |  |  | 250 |  | 50000 |  | 175 |  | 100 | [45 empty] | 380N | 1 | 3-1/2" | 4 #500 | #2
10 | 30.8 | 28 | 14 | 11 |  | 10 | 100 | 50 |  | Spare | 0 | 0 | NONE |  | M. ELEVATORS 620.14 |  |  | 500 |  |  | 333 |  | 65000 |  | 200 |  | 125 | [45 empty] | 400N | 2 | 2" | 4 #3/0 | #2
15 | 46.2 | 42 | 21 | 17 | [5 empty] | Space | 0 | 0 | NONE |  | Units ≥ | Factor |  | 750 |  |  | 500 |  | 85000 |  | 230 |  | 160 | [45 empty] | 500N | 2 | 2-1/2" | 4 #250 | #2
20 | 59.4 | 54 | 27 | 22 | [5 empty] | Panel | 1 | 0 | PNL |  | 1 | 1 |  | 1000 |  |  |  |  | 100000 |  | 250 |  | 200 | [45 empty] | 600N | 2 | 3" | 4 #350 | #1
25 | 74.8 | 68 | 34 | 27 | [5 empty] | Mixed REC/LTG | 1.25 | 0 | LTG |  | 2 | 0.95 |  | 1500 |  |  |  |  | 200000 |  | 300 |  | 225 | [45 empty] | 700N | 2 | 3" | 4 #500 | #1/0
30 | 88 | 80 | 40 | 32 | [10 empty] | 3 | 0.9 |  | 2000 | [6 empty] | 350 |  | 250 | [45 empty] | 760N | 2 | 3" | 4 #500 | #1/0
40 | 114 | 104 | 52 | 41 | [10 empty] | 4 | 0.85 |  | 2500 | [6 empty] | 400 |  | 300 | [45 empty] | 800N | 3 | 3" | 4 #300 | #1/0
50 | 143 | 130 | 65 | 52 | [10 empty] | 5 | 0.82 | [8 empty] | 500 |  | 400 | [45 empty] | 1000N | 3 | 3" | 4 #400 | #2/0
60 | 169 | 154 | 77 | 62 | [10 empty] | 6 | 0.79 | [8 empty] | 600 |  | 500 | [45 empty] | 1200N | 4 | 3" | 4 #350 | #3/0
75 | 211 | 192 | 96 | 77 | [10 empty] | 7 | 0.77 | [8 empty] | 750 |  | 625 | [45 empty] | 1600N | 5 | 3" | 4 #400 | #4/0
100 | 273 | 248 | 124 | 99 | [10 empty] | 8 | 0.75 | [8 empty] | 800 |  | 750 | [45 empty] | 2000N | 6 | 3" | 4 #400 | #250
125 | 343 | 312 | 156 | 125 | [10 empty] | 9 | 0.73 | [8 empty] | 1000 |  | 900 | [45 empty] | 2500N | 7 | 3-1/2" | 4 #500 | #350
150 | 396 | 360 | 180 | 144 | [10 empty] | 10 | 0.72 | [8 empty] | 1250 |  | 1100 | [45 empty] | 3000N | 8 | 3-1/2" | 4 #500 | #400
200 | 528 | 480 | 240 | 192 | [20 empty] | 1500 | [47 empty] | 3500N | 10 | 3-1/2" | 4 #500 | #500
250 |  | 604 | 302 | 242 | [20 empty] | 1750 | [47 empty] | 4000N | 11 | 3-1/2" | 4 #500 | #500
300 |  | 722 | 361 | 289 | [20 empty] | 2000 | [47 empty] | EXIST | EXISTING FEEDER TO REMAIN
350 |  | 828 | 414 | 336 | [20 empty] | 2500
400 |  | 954 | 477 | 382 | [20 empty] | 3000
450 |  | 1030 | 515 | 412
500 |  | 1180 | 590 | 472
Note on R5: SÄZÄN PowerCalc: Bussmann point-to-point C constant, 3 single conductors in steel conduit. VERIFY against current Bussmann/manufacturer data before use.
Note on S5: SÄZÄN PowerCalc: Bussmann point-to-point C constant, 3 single conductors in steel conduit. VERIFY against current Bussmann/manufacturer data before use.
Note on R6: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S6: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T6: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U6: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on CD6: SÄZÄN PowerCalc: Default transformer impedance used by the Transformer Schedule when %Z has not yet been entered for a detected transformer. 5.75% is a typical LV dry-type value; the schedule flags the blank input gold so the submittal value still gets entered.
Note on R7: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S7: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T7: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U7: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on CD7: SÄZÄN PowerCalc: Default upstream X/R ratio used by the Transformer Schedule when Source X/R has not been entered for a detected transformer. 15 is conservative for a stiff utility service.
Note on R8: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S8: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T8: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U8: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on AB8: SÄZÄN PowerCalc: BRANCH-circuit limit. Not a duplicate of Cfg_VDFeeder at CD15, which is the FEEDER limit — the two are different quantities that both happen to equal 3%. Read by the branch conductor sizing on all three TPL_ sheets. Basis: NEC 2023 210.19(A) Informational Note No. 4, 3 percent at the farthest outlet. Not enforceable per NEC 90.5; design standard.
Note on CD8: SÄZÄN PowerCalc: Magnetizing inrush estimate as a multiple of primary FLA, applied to every row of the Transformer Schedule (column AE). Drives primary device selection against nuisance tripping, and generator sizing where a transformer is on the emergency system. 8x to 12x is typical for dry-type units; 10x is a reasonable default. Use the manufacturer's inrush curve where it is available.
Note on R9: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S9: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T9: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U9: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on AB9: SÄZÄN PowerCalc: Was a hardcoded 0.05 duplicating Cfg_VDTotal at CD16. Both cells were labelled 'total' and both held 5%, so the workbook had two homes for one limit and a drift hazard. CD16 is now the single input; this cell links to it. Basis: NEC 2023 210.19(A) Informational Note No. 4 and 215.2(A)(1) Informational Note No. 2 — maximum total voltage drop on feeders plus branch circuits to the farthest outlet not exceeding 5 percent. Informational Notes are not enforceable requirements per NEC 90.5; this is a design standard.
Note on R10: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S10: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T10: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U10: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on CB10: SÄZÄN PowerCalc: Line-to-neutral voltage for each system. Used by the Short Circuit study: single-phase runs are calculated at line-to-neutral voltage with m = 2, three-phase at line-to-line with m = 1.732. For the 3-wire systems with no distributed neutral the value is the phase-to-ground potential, which is still the correct divisor for a line-to-ground fault calculation.
Note on CD10: SÄZÄN PowerCalc: System-wide capacity: the maximum number of equipment nodes the workbook supports. Governs the Equipment Registry depth, the Transformer / Feeder / Short Circuit / Voltage Drop schedule depths, and the tier-walk pass count (which self-limits to the actual node count, so a small project pays nothing for a high ceiling). Raising this means widening the registry and every dependent schedule together — see DESIGN_PtP_Model section 11.
Note on R11: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S11: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T11: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U11: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R12: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S12: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T12: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U12: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on CD12: SÄZÄN PowerCalc: Motor short-circuit contribution as a multiple of connected motor full-load amps, added to the bus fault before the interrupting-rating comparison. 4x is the common industry figure for induction motors (IEEE 141); use 5x on motor control centres or where a bus is dominated by large motors. Set per bus on the Short Circuit sheet where a specific bus differs.
Note on R13: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S13: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T13: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U13: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on CD13: SÄZÄN PowerCalc: Motor contribution multiplier applied automatically where the bus Type is MCC, on the basis that such a bus is motor-dominated. Overridable per bus.
Note on R14: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S14: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T14: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U14: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on BE14: SÄZÄN PowerCalc: Corrected: NEC Table 250.122 — 600 A OCPD requires 2/0 Al EGC (was duplicating the 1/0 value from the 500 A row).
Note on R15: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S15: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T15: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U15: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on CD15: SÄZÄN PowerCalc: FEEDER limit, per individual feeder run. Not a duplicate of VD_Branch at AB8, which is the BRANCH limit — different quantities, both 3%. Read by Feeder Schedule (V, BX), the Voltage Drop study (I), and since 2026-09-22 the feeder conductor sizing on all three TPL_ sheets. Basis: NEC 2023 215.2(A)(1) Informational Note No. 2. Not enforceable per NEC 90.5; design standard.
Note on R16: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S16: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T16: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U16: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on AA16: SÄZÄN PowerCalc: Per NEC 110.14(C): circuits ≤100 A sized off the 60°C ampacity column; >100 A use the configured termination temp column (Config). Min conductor #12 is an SGI design standard.
Note on CD16: SÄZÄN PowerCalc: COMBINED feeders-plus-branch limit, and the single home for this value — VD_Total at AB9 now links here rather than holding its own copy. Basis: NEC 2023 210.19(A) IN No. 4 / 215.2(A)(1) IN No. 2, 5 percent total to the farthest outlet. Not enforceable per NEC 90.5; design standard.
Note on R17: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S17: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T17: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U17: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R18: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S18: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T18: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U18: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R19: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S19: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T19: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U19: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R20: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S20: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T20: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U20: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R21: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S21: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T21: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U21: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R22: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S22: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T22: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U22: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R23: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S23: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T23: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U23: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R24: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S24: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T24: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U24: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R25: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S25: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T25: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U25: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R26: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S26: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T26: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U26: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R27: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S27: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T27: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U27: SÄZÄN PowerCalc: Interpolated by circular-mil area from the adjacent published rows — Bussmann Table 4 does not publish 700 or 800 kcmil. Formula, not a hardcode: see the cell. Source of the surrounding published values: Eaton/Bussmann Table 4, https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on R28: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on S28: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on T28: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on U28: SÄZÄN PowerCalc: Source: Eaton/Bussmann, Short-Circuit Current Calculations, Table 4 "C" Values for Conductors — Copper/Aluminum, 600V, three single conductors in conduit. https://www.eaton.com/content/dam/eaton/products/electrical-circuit-protection/fuses/solution-center/bus-ele-tech-lib-electrical-formulas.pdf
Note on K58: SÄZÄN PowerCalc: Mixed receptacle + lighting on one circuit: treated as continuous (125% sizing) and rolled into the Lighting demand bucket at 100% — receptacle portion conservatively gets no NEC 220.44 demand credit.

## Energy_Code_Data
INTERIOR LIGHTING POWER ALLOWANCES — WA STATE (WSEC) vs SEATTLE (SEC)
Reference tables only — do not edit. Table C405.4.2(1) and C405.4.2(2). Blank = that space type is not listed in that code.
A. BUILDING AREA METHOD — C405.4.2(1) |  |  | B. SPACE-BY-SPACE METHOD — C405.4.2(2) |  |  |  | C. ACTIVE SELECTION LIST
Building Area Type | WSEC (W/ft²) | SEC (W/ft²) | Space Type | WSEC (W/ft²) | SEC (W/ft²) | Group | Types available in the chosen code + method
Automotive facility | 0.64 | 0.69 | Atrium — Less than 20 feet in height | 0.39 | 0.3 | Common | Automotive facility
Convention center | 0.64 | 0.61 | Atrium — 20 to 40 feet in height | 0.48 | 0.39 | Common | Convention center
Court house | 0.79 | 0.71 | Atrium — Above 40 feet in height | 0.6 | 0.48 | Common | Court house
Dining: Bar lounge/leisure | 0.79 | 0.7 | Audience/seating area, permanent — In an auditorium | 0.61 | 0.54 | Common | Dining: Bar lounge/leisure
Dining: Cafeteria/fast food | 0.72 | 0.67 | Audience/seating area, permanent — In a gymnasium | 0.23 | 0.22 | Common | Dining: Cafeteria/fast food
Dining: Family | 0.71 | 0.62 | Audience/seating area, permanent — In a motion picture theater | 0.27 | 0.26 | Common | Dining: Family
Dormitory | 0.46 | 0.49 | Audience/seating area, permanent — In a penitentiary | 0.67 | 0.56 | Common | Dormitory
Exercise center | 0.67 | 0.68 | Audience/seating area, permanent — In a performing arts theater | 1.16 | 1.04 | Common | Exercise center
Fire station | 0.54 | 0.53 | Audience/seating area, permanent — In a religious building | 0.72 | 0.68 | Common | Fire station
Gymnasium | 0.75 | 0.71 | Audience/seating area, permanent — In a sports arena | 0.33 | 0.26 | Common | Gymnasium
Health care clinic | 0.7 | 0.77 | Audience/seating area, permanent — Otherwise | 0.23 | 0.22 | Common | Health care clinic
Hospital | 0.84 | 0.92 | Banking activity area | 0.61 |  | Common | Hospital
Hotel / motel | 0.56 | 0.5 | Classroom/lecture hall/training room — In a penitentiary | 0.89 | 0.74 | Common | Hotel / motel
Library | 0.83 | 0.79 | Classroom/lecture hall/training room — Otherwise | 0.71 | 0.68 | Common | Library
Manufacturing facility | 0.82 | 0.78 | Computer room, data center | 0.94 | 0.71 | Common | Manufacturing facility
Motion picture theater | 0.44 | 0.41 | Conference/meeting/multipurpose | 0.97 | 0.84 | Common | Motion picture theater
Multifamily | 0.41 | 0.44 | Confinement cell | 0.7 |  | Common | Multifamily
Museum | 0.55 | 0.53 | Copy/print room | 0.31 | 0.53 | Common | Museum
Office | 0.64 | 0.59 | Corridor — In a facility for the visually impaired (not primarily staff) | 0.71 | 0.71 | Common | Office
Parking garage | 0.14 | 0.16 | Corridor — In a hospital | 0.71 | 0.61 | Common | Parking garage
Penitentiary | 0.65 | 0.65 | Corridor — In a manufacturing facility | 0.41 |  | Common | Penitentiary
Performing arts theater | 0.84 | 0.78 | Corridor — Otherwise | 0.41 | 0.42 | Common | Performing arts theater
Police station | 0.66 | 0.59 | Courtroom | 1.2 | 1.03 | Common | Police station
Post office | 0.65 | 0.61 | Dining area — In a penitentiary | 0.42 | 0.35 | Common | Post office
Religious building | 0.67 | 0.63 | Dining area — In a facility for the visually impaired (not primarily staff) | 1.27 | 1.22 | Common | Religious building
Retail | 0.84 | 0.74 | Dining area — In a bar/lounge or leisure dining | 0.86 | 0.72 | Common | Retail
School/university | 0.7 | 0.67 | Dining area — In cafeteria or fast food dining | 0.4 | 0.34 | Common | School/university
Sports arena | 0.62 | 0.69 | Dining area — In a family dining area | 0.6 | 0.49 | Common | Sports arena
Town hall | 0.69 | 0.64 | Dining area — Otherwise | 0.43 | 0.4 | Common | Town hall
Transportation | 0.5 | 0.53 | Electrical/mechanical | 0.43 | 0.64 | Common | Transportation
Warehouse | 0.4 | 0.43 | Emergency vehicle garage | 0.52 | 0.48 | Common | Warehouse
Workshop | 0.91 | 0.82 | Food preparation | 1.09 | 1.13 | Common | Workshop
|  |  | Guest room | 0.41 |  | Common
|  |  | Laboratory — In or as a classroom | 1.11 | 1 | Common
|  |  | Laboratory — Otherwise | 1.33 | 1.14 | Common
|  |  | Laundry/washing area | 0.53 | 0.48 | Common
|  |  | Loading dock, interior | 0.88 | 0.83 | Common
|  |  | Lobby — In a facility for the visually impaired (not primarily staff) | 1.69 | 1.44 | Common
|  |  | Lobby — For an elevator | 0.65 | 0.61 | Common
|  |  | Lobby — In a hotel | 0.51 | 0.46 | Common
|  |  | Lobby — In a motion picture theater | 0.23 | 0.19 | Common
|  |  | Lobby — In a performing arts theater | 1.25 | 1.14 | Common
|  |  | Lobby — Otherwise | 0.84 | 0.76 | Common
|  |  | Locker room | 0.52 | 0.41 | Common
|  |  | Lounge/breakroom — In a health care facility | 0.42 | 0.77 | Common
|  |  | Lounge/breakroom — Otherwise | 0.59 | 0.52 | Common
|  |  | Office — Enclosed ≤ 250 ft² | 0.74 | 0.69 | Common
|  |  | Office — Enclosed > 250 ft² | 0.66 | 0.69 | Common
|  |  | Office — Open plan | 0.61 | 0.53 | Common
|  |  | Parking area, interior | 0.15 | 0.1 | Common
|  |  | Pharmacy area | 1.66 | 1.59 | Common
|  |  | Restroom — In a facility for the visually impaired (not primarily staff) | 1.26 | 0.96 | Common
|  |  | Restroom — Otherwise | 0.63 | 0.7 | Common
|  |  | Sales area | 1.05 | 0.81 | Common
|  |  | Seating area, general | 0.23 | 0.2 | Common
|  |  | Security screening — General area |  | 0.64 | Common
|  |  | Security screening — In transportation facilities |  | 0.93 | Common
|  |  | Security screening — Transportation waiting area |  | 0.56 | Common
|  |  | Stairwell | 0.49 | 0.45 | Common
|  |  | Storage room — Less than 50 ft² | 0.51 | 0.47 | Common
|  |  | Storage room — 50 to 100 ft² | 0.38 |  | Common
|  |  | Storage room — All other storage | 0.38 | 0.33 | Common
|  |  | Vehicular maintenance | 0.6 | 0.56 | Common
|  |  | Workshop | 1.26 | 1.11 | Common
|  |  | Convention center — Exhibit space | 0.61 | 0.48 | Building-specific
|  |  | Dormitory — Living quarters | 0.5 |  | Building-specific
|  |  | Facility for the visually impaired — In a chapel (not primarily staff) | 0.7 | 0.58 | Building-specific
|  |  | Facility for the visually impaired — In a recreation room (not primarily staff) | 1.77 | 1.2 | Building-specific
|  |  | Fire station — Sleeping quarters | 0.23 |  | Building-specific
|  |  | Gaming establishment — High limits game |  | 1.6 | Building-specific
|  |  | Gaming establishment — Slots |  | 0.51 | Building-specific
|  |  | Gaming establishment — Sportsbook |  | 0.78 | Building-specific
|  |  | Gaming establishment — Table games |  | 1.04 | Building-specific
|  |  | Gymnasium/fitness center — In an exercise area | 0.9 | 0.78 | Building-specific
|  |  | Gymnasium/fitness center — In a playing area | 0.85 | 0.78 | Building-specific
|  |  | Health care facility — In an exam/treatment room | 1.4 | 1.33 | Building-specific
|  |  | Health care facility — In an imaging room | 0.94 | 0.94 | Building-specific
|  |  | Health care facility — In a medical supply room | 0.62 | 0.56 | Building-specific
|  |  | Health care facility — In a nursery | 0.92 | 0.87 | Building-specific
|  |  | Health care facility — In a nurse's station | 1.17 | 1.07 | Building-specific
|  |  | Health care facility — In an operating room | 2.26 | 2.26 | Building-specific
|  |  | Health care facility — In a patient room | 0.68 |  | Building-specific
|  |  | Health care facility — In a physical therapy room | 0.91 | 0.82 | Building-specific
|  |  | Health care facility — In a recovery room | 1.25 | 1.18 | Building-specific
|  |  | Health care facility — In a telemedicine room |  | 1.44 | Building-specific
|  |  | Library — In a reading area | 0.96 | 0.82 | Building-specific
|  |  | Library — In the stacks | 1.1 | 1.12 | Building-specific
|  |  | Manufacturing facility — In a detailed manufacturing area | 0.8 | 0.71 | Building-specific
|  |  | Manufacturing facility — In an equipment room | 0.76 | 0.69 | Building-specific
|  |  | Manufacturing facility — In an extra high bay area (> 50 ft floor-ceiling) | 1.42 | 1.29 | Building-specific
|  |  | Manufacturing facility — In a high bay area (25–50 ft floor-ceiling) | 1.24 | 1.18 | Building-specific
|  |  | Manufacturing facility — In a low bay area (< 25 ft floor-ceiling) | 0.86 | 0.81 | Building-specific
|  |  | Museum — In a general exhibition area | 0.31 | 0.29 | Building-specific
|  |  | Museum — In a restoration room | 1.1 | 1.18 | Building-specific
|  |  | Performing arts theater — Dressing/fitting room | 0.41 | 0.37 | Building-specific
|  |  | Post office — Sorting area | 0.76 | 0.67 | Building-specific
|  |  | Religious building — In a fellowship hall | 0.54 | 0.48 | Building-specific
|  |  | Religious building — In a worship pulpit/choir area | 0.85 | 0.71 | Building-specific
|  |  | Retail — In a dressing/fitting room | 0.51 | 0.43 | Building-specific
|  |  | Retail — Hair salon |  | 0.62 | Building-specific
|  |  | Retail — Nail salon |  | 0.71 | Building-specific
|  |  | Retail — In a mall concourse | 0.82 | 0.54 | Building-specific
|  |  | Retail — Massage space |  | 0.77 | Building-specific
|  |  | Sports arena, playing area — Class 1 facility | 2.94 | 2.72 | Building-specific
|  |  | Sports arena, playing area — Class 2 facility | 2.01 | 1.88 | Building-specific
|  |  | Sports arena, playing area — Class 3 facility | 1.3 | 1.23 | Building-specific
|  |  | Sports arena, playing area — Class 4 facility | 0.86 | 0.81 | Building-specific
|  |  | Sports arena, pools — Class 1 facility |  | 2.09 | Building-specific
|  |  | Sports arena, pools — Class 2 facility |  | 1.4 | Building-specific
|  |  | Sports arena, pools — Class 3 facility |  | 0.94 | Building-specific
|  |  | Sports arena, pools — Class 4 facility |  | 0.56 | Building-specific
|  |  | Transportation — Airport hangar |  | 1.29 | Building-specific
|  |  | Transportation — In a baggage/carousel area | 0.39 | 0.27 | Building-specific
|  |  | Transportation — In an airport concourse | 0.25 | 0.47 | Building-specific
|  |  | Transportation — At a terminal ticket counter | 0.51 | 0.38 | Building-specific
|  |  | Transportation — Passenger loading area |  | 0.67 | Building-specific
|  |  | Warehouse, storage area — Medium to bulky palletized items | 0.33 | 0.31 | Building-specific
|  |  | Warehouse, storage area — Smaller, hand-carried items | 0.69 | 0.66 | Building-specific